## Sammary Sheet
ELECTRICAL LOAD LIST (Sammary sheet) | [5 empty] | Approved | K,Yoshimura |  |  | Co.,Ltd. Yoshimura Airchitecture Design Office Electro Systems Engineering Service | [5 empty] | Project name
[6 empty] | Checked | K,Sakai | Drawn | K,Sakai | [6 empty] | TGCRDL Relocation Project
ESE LOAD LIST-Ver 2.0 ('02.9/28)
Primary group No. | Sub- | Transformer |  |  |  | All Loads |  |  | with no Capacitor |  |  |  | with Capacitor |  |  |  | Capa- citor | Reactor | Note (Use)
| station | [7 empty] | Demand loads |  |  | Transformer | Demand loads |  |  | Transformer
| No. | TR.No. | Capacity | Classification | Type | [KW] | [KVar] | [KVA] | [KW] | [KVar] | [KVA] | Load factor [％] | [KW] | [KVar] | [KVA] | Load factor [％] | [KVar] | [KVar]
[KVA]
152-F13 | 9-2 S/S | 92-1 | 500 | Move (TG) | oil cooled | 234.169 | 176.295 | 293.1544 | 163.9183 | 123.4065 | 205.1789 | 41.0358 | 163.9183 | 123.4065 | 205.1789 | 41.0358 | 0 | 0 | Gasoline bench
152-F13 | 9-2 S/S | 92-2 | 500 | Move (TG) | oil cooled | 234.169 | 176.295 | 293.1544 | 163.9183 | 123.4065 | 205.1789 | 41.0358 | 163.9183 | 123.4065 | 205.1789 | 41.0358 | 0 | 0 | Diesel bench
152-F13 | 9-2 S/S | 92-3 | 500 | New | oil cooled | 343.9101 | 263.1157 | 433.3877 | 276.008 | 211.1526 | 347.5138 | 69.5028 | 276.008 | 211.1526 | 347.5138 | 69.5028 | 0 | 0 | #1･2-Power
152-F13 | 9-2 S/S | 92-4 | 500 | Move (Saitama) | oil cooled | 234.169 | 176.295 | 293.1544 | 163.9183 | 123.4065 | 205.1789 | 41.0358 | 163.9183 | 123.4065 | 205.1789 | 41.0358 | 0 | 0 | Fuel bench
(Subtotal) |  |  | 2000 |  |  | 1046.4169 | 792.0007 | 1312.851 | 767.7629 | 581.3721 | 963.0504 |  | 767.7629 | 581.3721 | 963.0504 |  | 0 | 0
152-F14 | 9-2 S/S | 92-5 | 300 | Move (TG) | oil cooled | 188.7771 | 176.7711 | 272.5409 | 143.2448 | 114.0379 | 183.0948 | 61.0316 | 143.2448 | 114.0379 | 183.0948 | 61.0316 | 0 | 0 | #1･2-Power & L.
152-F14 | 9-2 S/S | 92-6 | 750 | Move (Saitama) | oil cooled | 582.7007 | 429.9213 | 724.6784 | 407.8905 | 300.9449 | 506.895 | 300.9449 | 407.8905 | 300.9449 | 506.895 | 67.586 | 0 | 0 | ATF,GI-bench
152-F14 | 9-2 S/S | 92-7 | 500 | New | oil cooled | 340.3456 | 256.9035 | 426.5166 | 238.2419 | 179.8324 | 298.4944 | 179.8324 | 238.2419 | 179.8324 | 298.4944 | 59.6989 | 0 | 0 | Enduring bench
152-F14 | 9-2 S/S | 92-8 | 300 | New | oil cooled | 240 | 180 | 300 | 168 | 126 | 210 | 126 | 168 | 126 | 210 | 70 | 0 | 0 | Inst. PowerSupply
(Subtotal) |  |  | 1850 |  |  | 1351.8235 | 1043.5959 | 1723.7359 | 957.3773 | 720.8152 | 1198.4842 |  | 957.3773 | 720.8152 | 1198.4842 |  | 0 | 0
152-F01 | 8 S/S | 8-1 | 200 | Existing | (F)-molded | 179.01 | 212.3946 | 281.15 | 87.084 | 92.4552 | 127.0101 | 92.4552 | 87.084 | 92.4552 | 127.0101 | 63.5051 | 0 | 0 | #3,#4,#5-Lighting
152-F01 | 8 S/S | 8-3 | 500 | Move (TG) | oil cooled | 269.1096 | 189.5084 | 329.8272 | 188.3767 | 132.6559 | 230.3983 | 132.6559 | 188.3767 | 132.6559 | 230.3983 | 0 | 0 | 0 | CHDY-2
152-F01 | 8 S/S | 8-4 | 750 | New | oil cooled | 652.8169 | 531.0208 | 845.5944 | 391.7379 | 318.4152 | 504.8236 | 318.4152 | 391.7379 | 318.4152 | 504.8236 | 67.3098 | 0 | 0 | #3,#4,#5-Power
152-F01 | 8 S/S | 8-5 | 300 | Move (TG) | oil cooled | 232 | 174 | 290 | 162.4 | 121.8 | 203 | 121.8 | 162.4 | 121.8 | 203 | 67.6667 | 0 | 0 | CHDY Anal. PS
(Subtotal) |  |  | 1750 |  |  | 1332.9366 | 1106.9238 | 1746.5716 | 829.5987 | 665.3262 | 1065.232 |  | 829.5987 | 665.3262 | 1065.232 |  | 0 | 0
152-F09 | 8 S/S | 8-2 | 500 | Existing | (F)-molded | 558.3413 | 431.72 | 707.9779 | 226.6529 | 175.3795 | 286.5824 | 175.3795 | 226.6529 | 175.3795 | 286.5824 | 57.3165 | 0 | 0 | #3,#5-Power
152-F09 | 8 S/S | 8-6 | 600 | Move (Saitama) | oil cooled | 342.7938 | 244.7716 | 421.9325 | 239.9557 | 171.3401 | 294.8494 | 171.3401 | 239.9557 | 171.3401 | 294.8494 | 49.1416 | 0 | 0 | CHDY-1
152-F09 | 8 S/S | 8-7 | 500 | New | oil cooled | 404.596 | 266.9897 | 485.3818 | 283.3372 | 186.9828 | 339.4739 | 67.8948 | 283.3372 | 186.9828 | 339.4739 | 67.8948 | 0 | 0 | CVTDY,ATF-4
(Subtotal) |  |  | 1600 |  |  | 1305.7311 | 943.4812 | 1615.2922 | 749.9457 | 533.7024 | 920.9057 |  | 749.9457 | 533.7024 | 920.9057 |  | 0 | 0
152-F07-TR60 | 6 S/S | 6-1 | 100 | Exchange | oil cooled | 106.998 | 134.6256 | 173.07 | 47.5332 | 56.143 | 73.5625 | 73.5625 | 47.5332 | 56.143 | 73.5625 | 73.5625 | 0 | 0 | #6,#9-Lighting
152-F07-TR60 | 6 S/S | 6-2 | 150 | Existing | oil cooled | 159.4481 | 121.9037 | 203.0658 | 93.5701 | 71.8657 | 117.9832 | 78.6555 | 93.5701 | 71.8657 | 117.9832 | 78.6555 | 0 | 0 | #6,#9-Power
(Subtotal) |  |  | 250 |  |  | 266.4461 | 256.5293 | 376.1358 | 141.1033 | 128.0087 | 191.5457 |  | 141.1033 | 128.0087 | 191.5457 |  | 0 | 0
152-F03 | 7 S/S | 7-1 | 100 | Existing | oil cooled | 103.61 | 122.5122 | 162.45 | 50.672 | 53.4869 | 73.6784 | 73.6784 | 50.672 | 53.4869 | 73.6784 | 73.6784 | 0 | 0 | #7-Lighting
152-F03 | 7 S/S | 7-2 | 300 | New | oil cooled | 180.6751 | 233.5967 | 322.8744 | 114.1971 | 126.5873 | 170.4856 | 56.8285 | 114.1971 | 126.5873 | 170.4856 | 56.8285 | 0 | 0 | #7-Power
(Subtotal) |  |  | 400 |  |  | 284.2851 | 356.1089 | 485.3244 | 164.8691 | 180.0742 | 244.164 |  | 164.8691 | 180.0742 | 244.164 |  | 0 | 0
|  |  | [KVA] |  |  | [KW] | [KVar] | [KVA] | [KW] | [KVar] | [KVA] |  | [KW] | [KVar] | [KVA] |  | [KVar] | [KVar]
(SumTotal) |  |  | 7850 |  |  | 5587.6393 | 4498.6397 | 7259.9107 | 3610.657 | 2809.2987 | 4583.382 |  | 3610.657 | 2809.2987 | 4583.382 |  | 0 | 0

## Load-List
Prm.Group No. |  | 152-F13 |  | 3φ3W | 50 | All loads [KW] | 234.169 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 9-2 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 176.295 | TR. Load factor [％] |  |  | 41.0358 | TR. Load factor [％] |  |  | 41.0358 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 420 | All loads [KVA] | 293.1544 | Demand [KW] |  |  | 163.9183 | Demand [KW] |  |  | 163.9183 | Capacitor
Move (TG) |  | 92-1 |  | 500 |  | Installation place | Outdoors | Demand [KVar] |  |  | 123.4065 | Demand [KVar] |  |  | 123.4065 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 205.1789 | Demand [KVA] |  |  | 205.1789 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.7989 | Ave.Power factor |  |  | 0.7989 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
|  |  |  | Gasoline bench | [19 empty] | 0
0
91P1 |  |  | GA-ACDY | AC dynamo |  |  | others | 220 | 1 |  |  |  | 95 | 80 | 100 | 231.5789 |  |  | 0.7 | 162.1053 | 121.5789 | 202.6316 |  | 121.5789 | 231.5789 | 173.6842 | 289.4737
|  |  | GA-ACDY-F | Cooling fan of AC dynamo |  |  | IM-4P | 2.2 | 1 | 86.6653 | 72.1992 | 76.4463 |  |  |  | 1.9406 |  |  | 0.7 | 1.3584 | 1.3018 | 1.8815 |  | 1.3018 | 1.9406 | 1.8597 | 2.6878
|  |  | GA-ACDY-OP | Oil circulation pump of AC dynamo |  |  | IM-4P | 0.75 | 1 | 80.4909 | 65.4061 | 69.697 |  |  |  | 0.64942 |  |  | 0.7 | 0.4546 | 0.52576 | 0.69504 | 293.1[KVA](Df=1) | 0.52576 | 0.64942 | 0.75108 | 0.99291
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F13 |  | 3φ3W | 50 | All loads [KW] | 234.169 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 9-2 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 176.295 | TR. Load factor [％] |  |  | 41.0358 | TR. Load factor [％] |  |  | 41.0358 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 420 | All loads [KVA] | 293.1544 | Demand [KW] |  |  | 163.9183 | Demand [KW] |  |  | 163.9183 | Capacitor
Move (TG) |  | 92-2 |  | 500 |  | Installation place | Outdoors | Demand [KVar] |  |  | 123.4065 | Demand [KVar] |  |  | 123.4065 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 205.1789 | Demand [KVA] |  |  | 205.1789 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.7989 | Ave.Power factor |  |  | 0.7989 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
|  |  |  | Diesel bench | [19 empty] | 0
0
91P2 |  |  | DI-ACDY | AC dynamo |  |  | others | 220 | 1 |  |  |  | 95 | 80 | 100 | 231.5789 |  |  | 0.7 | 162.1053 | 121.5789 | 202.6316 |  | 121.5789 | 231.5789 | 173.6842 | 289.4737
|  |  | DI-ACDY-F | Cooling fan of AC dynamo |  |  | IM-4P | 2.2 | 1 | 86.6653 | 72.1992 | 76.4463 |  |  |  | 1.9406 |  |  | 0.7 | 1.3584 | 1.3018 | 1.8815 |  | 1.3018 | 1.9406 | 1.8597 | 2.6878
|  |  | DI-ACDY-OP | Oil circulation pump of AC dynamo |  |  | IM-4P | 0.75 | 1 | 80.4909 | 65.4061 | 69.697 |  |  |  | 0.64942 |  |  | 0.7 | 0.4546 | 0.52576 | 0.69504 | 293.1[KVA](Df=1) | 0.52576 | 0.64942 | 0.75108 | 0.99291
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F13 |  | 3φ3W | 50 | All loads [KW] | 343.9101 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 9-2 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 263.1157 | TR. Load factor [％] |  |  | 69.5028 | TR. Load factor [％] |  |  | 69.5028 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 210 | All loads [KVA] | 433.3877 | Demand [KW] |  |  | 276.008 | Demand [KW] |  |  | 276.008 | Capacitor
New |  | 92-3 |  | 500 |  | Installation place | Outdoors | Demand [KVar] |  |  | 211.1526 | Demand [KVar] |  |  | 211.1526 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 347.5138 | Demand [KVA] |  |  | 347.5138 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.79424 | Ave.Power factor |  |  | 0.79424 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
93P1 | side board |  | R-3-1 | Compressor (Heat pump package A/C) |  |  | IM-4P | 30 | 3 | 92.9242 | 80.0121 |  |  |  | 110 | 106.5384 |  |  | 0.8 | 85.2307 | 63.8961 | 106.5223 | Star delta starting | 63.8961 | 106.5384 | 79.8702 | 133.1528
| AC-M/C-R/M(2) |  |  | Cooling fan |  |  | IM-4P | 0.2 | 6 | 71.9545 | 65.0182 | 79.5455 |  |  |  | 1.3266 |  |  | 0.8 | 1.0613 | 1.2402 | 1.6323 |  | 1.2402 | 1.3266 | 1.5502 | 2.0403
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
93P2 | side board |  | R-3-2 | Compressor (Heat pump package A/C) |  |  | IM-4P | 30 | 3 | 92.9242 | 80.0121 |  |  |  | 110 | 106.5384 |  |  | 0.8 | 85.2307 | 63.8961 | 106.5223 | Star delta starting | 63.8961 | 106.5384 | 79.8702 | 133.1528
| AC-M/C-R/M(2) |  |  | Cooling fan |  |  | IM-4P | 0.2 | 6 | 71.9545 | 65.0182 | 79.5455 |  |  |  | 1.3266 |  |  | 0.8 | 1.0613 | 1.2402 | 1.6323 |  | 1.2402 | 1.3266 | 1.5502 | 2.0403
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
93P3 | #1･2P-3 |  | AHU-4 | Supply fan of Air-conditioning M/C |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.8 | 2.4649 | 2.3423 | 3.4003 |  | 2.3423 | 3.0811 | 2.9278 | 4.2504
| AC-M/C-R/M(2) |  | P-3-1 | Cold-water circulation pump |  |  | IM-4P | 7.5 | 1 | 89.4242 | 78.3939 | 78.7879 |  |  |  | 6.6079 |  |  | 0.8 | 5.2863 | 4.1865 | 6.7433 |  | 4.1865 | 6.6079 | 5.2331 | 8.4291
|  |  | P-3-2 | Cold-water circulation pump |  |  | IM-4P | 7.5 | 1 | 89.4242 | 78.3939 | 78.7879 |  |  |  | 6.6079 |  |  | 0.8 | 5.2863 | 4.1865 | 6.7433 |  | 4.1865 | 6.6079 | 5.2331 | 8.4291
|  |  | AHU-6 | Supply fan of Air-conditioning M/C |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.8 | 0.99327 | 1.2055 | 1.562 |  | 1.2055 | 1.2416 | 1.5068 | 1.9525
|  |  | R-4 | Water-cooled chiller |  |  | IM-4P | 15 | 1 | 92.2697 | 78.3788 | 78.7879 |  |  |  | 12.8083 |  |  | 0.8 | 10.2466 | 8.1189 | 13.0732 | Star delta starting | 8.1189 | 12.8083 | 10.1486 | 16.3415
|  |  | P-5 | Cold-water circulation pump |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.8 | 0.99327 | 1.2055 | 1.562 |  | 1.2055 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Automatic control power supply |  |  | others |  | 1 | [7 empty] | 2 | 80 | 1 | 1.6 | 1.2 | 2 |  | 0 | 1.6 | 1.2 | 2
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
93P4 | G93-ACG board |  |  | G93 Dynamo board | [19 empty] | 0
0
| G93-P1 |  | #1･2P-1 | Ventilation fan |  |  | IM-4P | 0.4 | 1 | 75.9818 | 65.8273 | 68.1818 |  |  |  | 0.35894 |  |  | 0.8 | 0.28715 | 0.32838 | 0.43622 |  | 0.32838 | 0.35894 | 0.41047 | 0.54527
|  |  | Entrs. Hall | Ventilation fan |  |  | IM-4P | 0.2 | 5 | 71.9545 | 65.0182 | 79.5455 |  |  |  | 1.1055 |  |  | 0.8 | 0.8844 | 1.0335 | 1.3602 |  | 1.0335 | 1.1055 | 1.2918 | 1.7003
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
| G93-P2 |  | #4P-1 | Ventilation fan |  |  | IM-4P | 0.18 | 1 |  |  |  | 70 | 65 | 70 | 0.18 |  |  | 0.8 | 0.144 | 0.16835 | 0.22154 |  | 0.16835 | 0.18 | 0.21044 | 0.27692
|  |  | Meter R/M | Ventilation fan |  |  | IM-4P | 0.1 | 2 |  |  |  | 65 | 65 | 70 | 0.21538 |  |  | 0.8 | 0.17231 | 0.20145 | 0.26509 |  | 0.20145 | 0.21538 | 0.25181 | 0.33136
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
| G93-P3 |  | #5P-1 | Ventilation fan |  |  | IM-4P | 0.2 | 1 | 71.9545 | 65.0182 | 79.5455 |  |  |  | 0.2211 |  |  | 0.8 | 0.17688 | 0.20669 | 0.27205 |  | 0.20669 | 0.2211 | 0.25837 | 0.34006
|  |  | Blend R/M(1) | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
G93P5 | #1･2P-6 |  | P-101 | Cold-water circulation pump |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.8 | 2.4649 | 2.3423 | 3.4003 |  | 2.3423 | 3.0811 | 2.9278 | 4.2504
| GearR/M-Roof |  | P-102 | Cold-water circulation pump |  |  | IM-4P | 22 | 1 | 93.0612 | 81.5967 | 83.6777 |  |  |  | 19.7817 |  |  | 0.8 | 15.8254 | 11.212 | 19.3946 |  | 11.212 | 19.7817 | 14.015 | 24.2433
|  |  | P-103 | Cold-water circulation pump |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.8 | 2.4649 | 2.3423 | 3.4003 |  | 2.3423 | 3.0811 | 2.9278 | 4.2504
|  |  | C-101 | Water-cooled chiller |  |  | IM-4P | 52.5 | 1 |  |  |  | 90 | 80 | 110 | 64.1667 |  |  | 0.8 | 51.3333 | 38.5 | 64.1667 |  | 38.5 | 64.1667 | 48.125 | 80.2083
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F13 |  | 3φ3W | 50 | All loads [KW] | 234.169 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 9-2 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 176.295 | TR. Load factor [％] |  |  | 41.0358 | TR. Load factor [％] |  |  | 41.0358 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 420 | All loads [KVA] | 293.1544 | Demand [KW] |  |  | 163.9183 | Demand [KW] |  |  | 163.9183 | Capacitor
Move (Saitama) |  | 92-4 |  | 500 |  | Installation place | Outdoors | Demand [KVar] |  |  | 123.4065 | Demand [KVar] |  |  | 123.4065 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 205.1789 | Demand [KVA] |  |  | 205.1789 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.7989 | Ave.Power factor |  |  | 0.7989 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
|  |  |  | Fuel bench | [19 empty] | 0
0
91P3 |  |  | FU-ACDY | AC dynamo |  |  | others | 220 | 1 |  |  |  | 95 | 80 | 100 | 231.5789 |  |  | 0.7 | 162.1053 | 121.5789 | 202.6316 |  | 121.5789 | 231.5789 | 173.6842 | 289.4737
|  |  | FU-ACDY-F | Cooling fan of AC dynamo |  |  | IM-4P | 2.2 | 1 | 86.6653 | 72.1992 | 76.4463 |  |  |  | 1.9406 |  |  | 0.7 | 1.3584 | 1.3018 | 1.8815 |  | 1.3018 | 1.9406 | 1.8597 | 2.6878
|  |  | FU-ACDY-OP | Oil circulation pump of AC dynamo |  |  | IM-4P | 0.75 | 1 | 80.4909 | 65.4061 | 69.697 |  |  |  | 0.64942 |  |  | 0.7 | 0.4546 | 0.52576 | 0.69504 | 293.1[KVA](Df=1) | 0.52576 | 0.64942 | 0.75108 | 0.99291
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F14 |  | 3φ3W | 50 | All loads [KW] | 188.7771 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 9-2 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 176.7711 | TR. Load factor [％] |  |  | 61.0316 | TR. Load factor [％] |  |  | 61.0316 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 210/105 | All loads [KVA] | 272.5409 | Demand [KW] |  |  | 143.2448 | Demand [KW] |  |  | 143.2448 | Capacitor
Move (TG) |  | 92-5 |  | 300 |  | Installation place | in boad | Demand [KVar] |  |  | 114.0379 | Demand [KVar] |  |  | 114.0379 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 183.0948 | Demand [KVA] |  |  | 183.0948 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.78235 | Ave.Power factor |  |  | 0.78235 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
95P1 | #1･2P-1 |  |  | No.1～No.6 bench wall socket |  |  | others |  | 6 | [7 empty] | 2.2 | 0.8 | 0.4 | 0.04224 | 5.2798 | 5.28 |  | 0 | 0.1056 | 13.1996 | 13.2
| Entrs. hall |  |  | No.1～No.6 Overhead traveling crane |  |  | IM-4P |  | 6 | [7 empty] | 2.7 | 0.8 | 0.05 | 0.00648 | 0.80997 | 0.81 |  | 0 | 0.1296 | 16.1995 | 16.2
|  |  | 12SS-1 | No.5 bench Electric shutter |  |  | IM-4P | 0.4 | 1 | 75.9818 | 65.8273 | 68.1818 |  |  |  | 0.35894 |  |  | 0.05 | 0.017947 | 0.020523 | 0.027264 |  | 0.020523 | 0.35894 | 0.41047 | 0.54527
|  |  | AC-109 | Air-conditioning M/C (open bench) |  |  | IM-4P | 5.21 | 1 |  |  |  | 85 | 75 | 100 | 6.1294 |  |  | 0.8 | 4.9035 | 4.3245 | 6.538 |  | 4.3245 | 6.1294 | 5.4056 | 8.1725
|  |  | AC-119 | Air-conditioning M/C (Analysis R/M) |  |  | IM-4P | 6.82 | 1 |  |  |  | 85 | 75 | 100 | 8.0235 |  |  | 0.8 | 6.4188 | 5.6609 | 8.5584 |  | 5.6609 | 8.0235 | 7.0761 | 10.698
|  |  | AC-100 | Air-conditioning M/C (Electric R/M) |  |  | IM-4P | 2.95 | 1 |  |  |  | 75 | 70 | 100 | 3.9333 |  |  | 0.8 | 3.1467 | 3.2102 | 4.4952 |  | 3.2102 | 3.9333 | 4.0128 | 5.619
|  |  | AC-110 | Air-conditioning M/C (No.3 bench) |  |  | IM-4P | 4.97 | 1 |  |  |  | 85 | 75 | 100 | 5.8471 |  |  | 0.8 | 4.6776 | 4.1253 | 6.2369 |  | 4.1253 | 5.8471 | 5.1566 | 7.7961
|  |  | AC-120 | Air-conditioning M/C (Part warehouse) |  |  | IM-4P | 3.75 | 1 |  |  |  | 75 | 70 | 100 | 5 |  |  | 0.8 | 4 | 4.0808 | 5.7143 |  | 4.0808 | 5 | 5.101 | 7.1429
|  |  | EF-29,3 | Exhaust fan |  |  | IM-4P | 0.2 | 3 | 71.9545 | 65.0182 | 79.5455 |  |  |  | 0.6633 |  |  | 0.8 | 0.53064 | 0.62008 | 0.81614 |  | 0.62008 | 0.6633 | 0.77511 | 1.0202
|  |  | EF-4 | Exhaust fan |  |  | IM-4P | 0.4 | 2 | 75.9818 | 65.8273 | 68.1818 |  |  |  | 0.71788 |  |  | 0.8 | 0.5743 | 0.65675 | 0.87243 |  | 0.65675 | 0.71788 | 0.82094 | 1.0905
|  |  | EF-1,2,17 | Exhaust fan |  |  | IM-4P | 0.75 | 6 | 80.4909 | 65.4061 | 69.697 |  |  |  | 3.8965 |  |  | 0.8 | 3.1172 | 3.6052 | 4.766 |  | 3.6052 | 3.8965 | 4.5065 | 5.9575
|  |  | EF-27,28 | Exhaust fan |  |  | IM-4P | 0.75 | 5 | 80.4909 | 65.4061 | 69.697 |  |  |  | 3.2471 |  |  | 0.8 | 2.5977 | 3.0043 | 3.9716 |  | 3.0043 | 3.2471 | 3.7554 | 4.9646
|  |  | DC-01,02 | Draft chamber |  |  | IM-4P | 0.2 | 2 | 71.9545 | 65.0182 | 79.5455 |  |  |  | 0.4422 |  |  | 0.8 | 0.35376 | 0.41339 | 0.54409 |  | 0.41339 | 0.4422 | 0.51674 | 0.68011
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
95P2 | #1･2P-2 |  | AHU-3 | Supply fan of Air-conditioning M/C |  |  | IM-4P | 37 | 1 | 93.9953 | 85.5894 | 82.3096 |  |  |  | 32.4001 |  |  | 0.8 | 25.92 | 15.6615 | 30.2842 | Star delta starting | 15.6615 | 32.4001 | 19.5768 | 37.8552
| 2F-CTRL R/M |  | ----- | Automatic control power supply |  |  | others |  | 1 | [7 empty] | 2 | 0.8 | 0.8 | 0.0128 | 1.5999 | 1.6 |  | 0 | 0.016 | 1.9999 | 2
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 0.8 | 1 | 0.004 | 0.49998 | 0.5 |  | 0 | 0.004 | 0.49998 | 0.5
0
0
0
0
0
95P3 | #1･2P-4 |  | CT1-1 | Cooling tower fan |  |  | IM-4P | 3.5 | 1 |  |  |  | 87 | 72 | 72 | 2.8966 |  |  | 0.8 | 2.3172 | 2.2335 | 3.2184 |  | 2.2335 | 2.8966 | 2.7918 | 4.023
| Exts. Roof |  | EH1-1 | Freeze prevention heater |  |  | hearter |  | 1 | [7 empty] | 5 | 95 | 0.8 | 3.8 | 1.249 | 4 |  | 0 | 4.75 | 1.5612 | 5
|  |  | CT1-2 | Cooling tower fan |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.8 | 2.4649 | 2.3423 | 3.4003 |  | 2.3423 | 3.0811 | 2.9278 | 4.2504
|  |  | EH1-2 | Freeze prevention heater |  |  | hearter |  | 1 | [7 empty] | 5 | 95 | 0.8 | 3.8 | 1.249 | 4 |  | 0 | 4.75 | 1.5612 | 5
|  |  | P4-1 | Cooling-water circulation pump |  |  | IM-4P | 11 | 1 | 91.8769 | 76.4587 | 76.4463 |  |  |  | 9.1526 |  |  | 0.8 | 7.3221 | 6.1722 | 9.5765 | Star delta starting | 6.1722 | 9.1526 | 7.7153 | 11.9706
|  |  | P4-2 | Cooling-water circulation pump |  |  | IM-4P | 11 | 1 | 91.8769 | 76.4587 | 76.4463 |  |  |  | 9.1526 |  |  | 0.8 | 7.3221 | 6.1722 | 9.5765 | Star delta starting | 6.1722 | 9.1526 | 7.7153 | 11.9706
|  |  | P6 | Cooling-water circulation pump |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.8 | 0.99327 | 1.2055 | 1.562 |  | 1.2055 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Automatic control power supply |  |  | others |  | 1 | [7 empty] | 2 | 80 | 0.8 | 1.28 | 0.96 | 1.6 |  | 0 | 1.6 | 1.2 | 2
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
0
0
0
95P4 | #1･2P-5 |  |  | AC Generator |  |  | others | 7.5 | 4 |  |  |  | 85 | 80 | 100 | 35.2941 |  |  | 0.7 | 24.7059 | 18.5294 | 30.8824 |  | 18.5294 | 35.2941 | 26.4706 | 44.1176
| Open bench |  |  | Overhead traveling crane (open bench) |  |  | IM-4P | 2.7 | 1 |  |  |  | 75 | 70 | 80 | 2.88 |  |  | 0.05 | 0.144 | 0.14691 | 0.20571 |  | 0.14691 | 2.88 | 2.9382 | 4.1143
0
0
0
0
0
95L1 | #1･2L-1 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 33.48 | 90 | 0.9 | 27.1188 | 13.1342 | 30.132 |  | 0 | 30.132 | 14.5936 | 33.48
| Entrs. hall |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 20.22 | 60 | 0.4 | 4.8528 | 6.4704 | 8.088 |  | 0 | 12.132 | 16.176 | 20.22
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F14 |  | 3φ3W | 50 | All loads [KW] | 582.7007 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 9-2 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 429.9213 | TR. Load factor [％] |  |  | 67.586 | TR. Load factor [％] |  |  | 67.586 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 420 | All loads [KVA] | 724.6784 | Demand [KW] |  |  | 407.8905 | Demand [KW] |  |  | 407.8905 | Capacitor
Move (Saitama) |  | 92-6 |  | 750 |  | Installation place | in boad | Demand [KVar] |  |  | 300.9449 | Demand [KVar] |  |  | 300.9449 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 506.895 | Demand [KVA] |  |  | 506.895 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.80468 | Ave.Power factor |  |  | 0.80468 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
|  |  |  | ATF-bench | [19 empty] | 0
96P1 |  |  | ATF-ACDY-1 | DC dynamo |  |  | others | 110 | 1 |  |  |  | 90 | 80 | 100 | 122.2222 |  |  | 0.7 | 85.5556 | 64.1667 | 106.9444 |  | 64.1667 | 122.2222 | 91.6667 | 152.7778
|  |  | ATF-ACDY-F1 | Cooling fan of DC dynamo |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.7 | 2.1568 | 2.0495 | 2.9753 |  | 2.0495 | 3.0811 | 2.9278 | 4.2504
|  |  | ATF-ACDY-OP | Oil circulation pump of DC dynamo |  |  | IM-4P | 1 | 1 |  |  |  | 80 | 63 | 68 | 0.85 |  |  | 0.7 | 0.595 | 0.73345 | 0.94444 | 158.3[KVA](Df=1) | 0.73345 | 0.85 | 1.0478 | 1.3492
0
0
0
0
|  |  |  | ATF-bench | [19 empty] | 0
96P2 |  |  | ATF-ACDY-2 | DC dynamo |  |  | others | 110 | 1 |  |  |  | 90 | 80 | 100 | 122.2222 |  |  | 0.7 | 85.5556 | 64.1667 | 106.9444 |  | 64.1667 | 122.2222 | 91.6667 | 152.7778
|  |  | ATF-ACDY-F2 | Cooling fan of DC dynamo |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.7 | 2.1568 | 2.0495 | 2.9753 | 157[KVA](Df=1) | 2.0495 | 3.0811 | 2.9278 | 4.2504
0
0
0
0
|  |  |  | Gear-bench | [19 empty] | 0
96P3 |  |  | GI-ACDY-1 | DC dynamo |  |  | others | 110 | 1 |  |  |  | 90 | 80 | 100 | 122.2222 |  |  | 0.7 | 85.5556 | 64.1667 | 106.9444 |  | 64.1667 | 122.2222 | 91.6667 | 152.7778
|  |  | GI-ACDY-F1 | Cooling fan of DC dynamo |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.7 | 2.1568 | 2.0495 | 2.9753 |  | 2.0495 | 3.0811 | 2.9278 | 4.2504
|  |  | GI-ACDY-OP | Oil circulation pump of DC dynamo |  |  | IM-4P | 1 | 1 |  |  |  | 80 | 63 | 68 | 0.85 |  |  | 0.7 | 0.595 | 0.73345 | 0.94444 | 158.3[KVA](Df=1) | 0.73345 | 0.85 | 1.0478 | 1.3492
0
0
0
0
|  |  |  | Gear-bench | [19 empty] | 0
96P4 |  |  | GI-ACDY-2 | DC dynamo |  |  | others | 110 | 1 |  |  |  | 90 | 80 | 100 | 122.2222 |  |  | 0.7 | 85.5556 | 64.1667 | 106.9444 |  | 64.1667 | 122.2222 | 91.6667 | 152.7778
|  |  | GI-ACDY-F2 | Cooling fan of DC dynamo |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.7 | 2.1568 | 2.0495 | 2.9753 | 152.7[KVA](Df=1) | 2.0495 | 3.0811 | 2.9278 | 4.2504
0
0
0
0
96P5 |  |  |  | Gear moter |  |  | IM | 75 | 1 |  |  |  | 94 | 85 | 100 | 79.7872 |  |  | 0.7 | 55.8511 | 34.6134 | 65.7071 |  | 34.6134 | 79.7872 | 49.4477 | 93.8673
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F14 |  | 3φ3W | 50 | All loads [KW] | 340.3456 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 9-2 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 256.9035 | TR. Load factor [％] |  |  | 59.6989 | TR. Load factor [％] |  |  | 59.6989 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 550 | All loads [KVA] | 426.5166 | Demand [KW] |  |  | 238.2419 | Demand [KW] |  |  | 238.2419 | Capacitor
New |  | 92-7 |  | 500 |  | Installation place | in boad | Demand [KVar] |  |  | 179.8324 | Demand [KVar] |  |  | 179.8324 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 298.4944 | Demand [KVA] |  |  | 298.4944 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.79815 | Ave.Power factor |  |  | 0.79815 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
|  |  |  | Enduring bench | [19 empty] | 0
0
97P1 |  |  | EN-ACDY | DC dynamo |  |  | others | 300 | 1 |  |  |  | 90 | 80 | 100 | 333.3333 |  |  | 0.7 | 233.3333 | 175 | 291.6667 |  | 175 | 333.3333 | 250 | 416.6667
|  |  | EN-ACDY-F1 | Cooling fan of DC dynamo |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.7 | 2.1568 | 2.0495 | 2.9753 |  | 2.0495 | 3.0811 | 2.9278 | 4.2504
|  |  | EN-ACDY-F2 | Cooling fan of DC dynamo |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.7 | 2.1568 | 2.0495 | 2.9753 |  | 2.0495 | 3.0811 | 2.9278 | 4.2504
|  |  | EN-ACDY-OP | Oil circulation pump of DC dynamo |  |  | IM-4P | 1 | 1 |  |  |  | 80 | 63 | 68 | 0.85 |  |  | 0.7 | 0.595 | 0.73345 | 0.94444 | 426.5[KVA](Df=1) | 0.73345 | 0.85 | 1.0478 | 1.3492
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F14 |  | 3φ3W | 50 | All loads [KW] | 240 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 9-2 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 180 | TR. Load factor [％] |  |  | 70 | TR. Load factor [％] |  |  | 70 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 210 | All loads [KVA] | 300 | Demand [KW] |  |  | 168 | Demand [KW] |  |  | 168 | Capacitor
New |  | 92-8 |  | 300 |  | Installation place | in boad | Demand [KVar] |  |  | 126 | Demand [KVar] |  |  | 126 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 210 | Demand [KVA] |  |  | 210 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.8 | Ave.Power factor |  |  | 0.8 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
98P1 | Ins. Board |  |  | Instrumentation power supply |  |  | others |  | 1 | [7 empty] | 300 | 80 | 0.7 | 168 | 126 | 210 |  | 0 | 240 | 180 | 300
| 1F-CTRL R/M |  |  | (for each benches) | [19 empty] | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F01 |  | 1φ3W | 50 | All loads [KW] | 179.01 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 8 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 212.3946 | TR. Load factor [％] |  |  | 63.5051 | TR. Load factor [％] |  |  | 63.5051 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 210/105 | All loads [KVA] | 281.15 | Demand [KW] |  |  | 87.084 | Demand [KW] |  |  | 87.084 | Capacitor
Existing |  | 8-1 |  | 200 |  | Installation place | in boad | Demand [KVar] |  |  | 92.4552 | Demand [KVar] |  |  | 92.4552 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 127.0101 | Demand [KVA] |  |  | 127.0101 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | (F)-molded |  | Ave.Power factor |  |  | 0.68565 | Ave.Power factor |  |  | 0.68565 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
81L1-01 | #3L-12,11 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 7.15 | 90 | 0.9 | 5.7915 | 2.805 | 6.435 |  | 0 | 6.435 | 3.1166 | 7.15
| R/M-103･102 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 8.65 | 60 | 0.4 | 2.076 | 2.768 | 3.46 |  | 0 | 5.19 | 6.92 | 8.65
0
81L1-02 | #3L-13,14,15 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 4.7 | 90 | 0.9 | 3.807 | 1.8438 | 4.23 |  | 0 | 4.23 | 2.0487 | 4.7
| 106･107･108 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 14.9 | 60 | 0.4 | 3.576 | 4.768 | 5.96 |  | 0 | 8.94 | 11.92 | 14.9
0
81L1-03 | #3L-K1,17,16 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 3.75 | 90 | 0.9 | 3.0375 | 1.4711 | 3.375 |  | 0 | 3.375 | 1.6346 | 3.75
| Pas･112･110 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 21.25 | 60 | 0.4 | 5.1 | 6.8 | 8.5 |  | 0 | 12.75 | 17 | 21.25
0
81L1-04 | #3L-18,19 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 2.8 | 90 | 0.9 | 2.268 | 1.0984 | 2.52 |  | 0 | 2.52 | 1.2205 | 2.8
| 114･115 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 25.2 | 60 | 0.4 | 6.048 | 8.064 | 10.08 |  | 0 | 15.12 | 20.16 | 25.2
0
81L1-05 | #3L-27 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 0.8 | 90 | 0.9 | 0.648 | 0.31384 | 0.72 |  | 0 | 0.72 | 0.34871 | 0.8
| 209 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 6.6 | 60 | 0.4 | 1.584 | 2.112 | 2.64 |  | 0 | 3.96 | 5.28 | 6.6
0
0
81L2-01 | #3L-31,21 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 1.6 | 90 | 0.9 | 1.296 | 0.62768 | 1.44 |  | 0 | 1.44 | 0.69742 | 1.6
| 213･201 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 15.45 | 60 | 0.4 | 3.708 | 4.944 | 6.18 |  | 0 | 9.27 | 12.36 | 15.45
0
81L2-02 | #3L-22 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 1.2 | 90 | 0.9 | 0.972 | 0.47076 | 1.08 |  | 0 | 1.08 | 0.52307 | 1.2
| 202 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 21.05 | 60 | 0.4 | 5.052 | 6.736 | 8.42 |  | 0 | 12.63 | 16.84 | 21.05
0
81L2-03 | #3L-23 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 0.9 | 90 | 0.9 | 0.729 | 0.35307 | 0.81 |  | 0 | 0.81 | 0.3923 | 0.9
| 203 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 18.2 | 60 | 0.4 | 4.368 | 5.824 | 7.28 |  | 0 | 10.92 | 14.56 | 18.2
0
81L2-04 | #3L-30 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 1 | 90 | 0.9 | 0.81 | 0.3923 | 0.9 |  | 0 | 0.9 | 0.43589 | 1
| 212 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 30.5 | 60 | 0.4 | 7.32 | 9.76 | 12.2 |  | 0 | 18.3 | 24.4 | 30.5
0
0
81L3-01 | #3L-29,24 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 2.1 | 90 | 0.9 | 1.701 | 0.82383 | 1.89 |  | 0 | 1.89 | 0.91537 | 2.1
| 211･204 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 17.9 | 60 | 0.4 | 4.296 | 5.728 | 7.16 |  | 0 | 10.74 | 14.32 | 17.9
0
81L3-02 | #3L-28,25 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 1.8 | 90 | 0.9 | 1.458 | 0.70614 | 1.62 |  | 0 | 1.62 | 0.7846 | 1.8
| 210ﾒ206 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 21.9 | 60 | 0.4 | 5.256 | 7.008 | 8.76 |  | 0 | 13.14 | 17.52 | 21.9
0
81L3-03 | #3L-26 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 0.9 | 90 | 0.9 | 0.729 | 0.35307 | 0.81 |  | 0 | 0.81 | 0.3923 | 0.9
| 207 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 34.4 | 60 | 0.4 | 8.256 | 11.008 | 13.76 |  | 0 | 20.64 | 27.52 | 34.4
0
81L3-04 | #3L-K2,K3 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 5.7 | 90 | 0.9 | 4.617 | 2.2361 | 5.13 |  | 0 | 5.13 | 2.4846 | 5.7
| Pas･208 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 10.75 | 60 | 0.4 | 2.58 | 3.44 | 4.3 |  | 0 | 6.45 | 8.6 | 10.75
0
0
0
Prm.Group No. |  | 152-F01 |  | 3φ3W | 50 | All loads [KW] | 269.1096 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 8 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 189.5084 | TR. Load factor [％] |  |  | 46.0797 | TR. Load factor [％] |  |  | 46.0797 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 420 | All loads [KVA] | 329.8272 | Demand [KW] |  |  | 188.3767 | Demand [KW] |  |  | 188.3767 | Capacitor
Move (TG) |  | 8-3 |  | 500 |  | Installation place | Outdoors | Demand [KVar] |  |  | 132.6559 | Demand [KVar] |  |  | 132.6559 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 230.3983 | Demand [KVA] |  |  | 230.3983 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.81761 | Ave.Power factor |  |  | 0.81761 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
|  |  |  | No.2 Chassis Dynamo equipment | [19 empty] | 0
0
83P1 | No.2 CHDY |  | CHDY2 | No.2 Chassis Dynamo |  |  | others | 150 | 1 |  |  |  | 95 | 80 | 100 | 157.8947 |  |  | 0.7 | 110.5263 | 82.8947 | 138.1579 |  | 82.8947 | 157.8947 | 118.4211 | 197.3684
| Switchboard place |  | CHDY2-CF | Dynamo E/G cooling fan |  |  | IM-4P | 90 | 1 |  |  |  | 93 | 86 | 100 | 96.7742 |  |  | 0.7 | 67.7419 | 40.1957 | 78.7697 |  | 40.1957 | 96.7742 | 57.4224 | 112.5281
|  |  | CHDY2-F1 | Dynamo cooling fan-No.1 |  |  | IM-4P | 5.5 | 1 | 89.2835 | 75.881 | 76.0331 |  |  |  | 4.6838 |  |  | 0.7 | 3.2786 | 2.8142 | 4.3207 |  | 2.8142 | 4.6838 | 4.0202 | 6.1725
|  |  | CHDY2-F2 | Dynamo cooling fan-No.2 |  |  | IM-4P | 5.5 | 1 | 89.2835 | 75.881 | 76.0331 |  |  |  | 4.6838 |  |  | 0.7 | 3.2786 | 2.8142 | 4.3207 |  | 2.8142 | 4.6838 | 4.0202 | 6.1725
|  |  | CHDY2-F3 | Dynamo cooling fan-No.3 |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.7 | 0.86911 | 1.0548 | 1.3667 |  | 1.0548 | 1.2416 | 1.5068 | 1.9525
|  |  | CHDY2-M1 | Dynamo roller movement equipment |  |  | IM-4P | 2.2 | 1 | 86.6653 | 72.1992 | 76.4463 |  |  |  | 1.9406 |  |  | 0.7 | 1.3584 | 1.3018 | 1.8815 |  | 1.3018 | 1.9406 | 1.8597 | 2.6878
|  |  | CHDY2-M2 | Dynamo E/G-CF movement equipment |  |  | IM-4P | 0.75 | 1 | 80.4909 | 65.4061 | 69.697 |  |  |  | 0.64942 |  |  | 0.7 | 0.4546 | 0.52576 | 0.69504 |  | 0.52576 | 0.64942 | 0.75108 | 0.99291
|  |  | CHDY2-P1 | Dynamo lubricating oil pump-No.1 |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.7 | 0.86911 | 1.0548 | 1.3667 | 329.8[KVA](Df=1) | 1.0548 | 1.2416 | 1.5068 | 1.9525
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F01 |  | 3φ3W | 50 | All loads [KW] | 652.8169 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 8 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 531.0208 | TR. Load factor [％] |  |  | 67.3098 | TR. Load factor [％] |  |  | 67.3098 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 210 | All loads [KVA] | 845.5944 | Demand [KW] |  |  | 391.7379 | Demand [KW] |  |  | 391.7379 | Capacitor
New |  | 8-4 |  | 750 |  | Installation place | Outdoors | Demand [KVar] |  |  | 318.4152 | Demand [KVar] |  |  | 318.4152 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 504.8236 | Demand [KVA] |  |  | 504.8236 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.77599 | Ave.Power factor |  |  | 0.77599 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
84P1 | #3P-R1 |  | AC-139 | Air-conditioning exterior unit |  |  | IM-4P | 4.97 | 1 |  |  |  | 85 | 73 | 100 | 5.8471 |  |  | 0.6 | 3.5082 | 3.2845 | 4.8058 |  | 3.2845 | 5.8471 | 5.4742 | 8.0097
| #3 BLDG roof |  | AC-122 | Air-conditioning exterior unit |  |  | IM-4P | 3.21 | 1 |  |  |  | 85 | 73 | 100 | 3.7765 |  |  | 0.6 | 2.2659 | 2.1214 | 3.1039 |  | 2.1214 | 3.7765 | 3.5356 | 5.1732
|  |  | AC-128 | Air-conditioning exterior unit |  |  | IM-4P | 3.67 | 1 |  |  |  | 85 | 73 | 100 | 4.3176 |  |  | 0.6 | 2.5906 | 2.4254 | 3.5488 |  | 2.4254 | 4.3176 | 4.0423 | 5.9146
|  |  | EH-128 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 2.1 | 95 | 0.6 | 1.197 | 0.39343 | 1.26 |  | 0 | 1.995 | 0.65572 | 2.1
|  |  | AC114 | Air-conditioning exterior unit |  |  | IM-4P | 1.98 | 1 |  |  |  | 80 | 70 | 100 | 2.475 |  |  | 0.6 | 1.485 | 1.515 | 2.1214 |  | 1.515 | 2.475 | 2.525 | 3.5357
|  |  | AC155 | Air-conditioning exterior unit |  |  | IM-4P | 4.52 | 1 |  |  |  | 85 | 73 | 100 | 5.3176 |  |  | 0.6 | 3.1906 | 2.9871 | 4.3707 |  | 2.9871 | 5.3176 | 4.9785 | 7.2844
|  |  | AC-115 | Air-conditioning exterior unit |  |  | IM-4P | 2.1 | 1 |  |  |  | 80 | 70 | 100 | 2.625 |  |  | 0.6 | 1.575 | 1.6068 | 2.25 |  | 1.6068 | 2.625 | 2.678 | 3.75
|  |  | EH-115 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 2.1 | 95 | 0.6 | 1.197 | 0.39343 | 1.26 |  | 0 | 1.995 | 0.65572 | 2.1
|  |  | AC-121 | Air-conditioning exterior unit |  |  | IM-4P | 2.95 | 1 |  |  |  | 80 | 70 | 100 | 3.6875 |  |  | 0.6 | 2.2125 | 2.2572 | 3.1607 |  | 2.2572 | 3.6875 | 3.762 | 5.2679
|  |  | EH-124 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 2.1 | 95 | 0.6 | 1.197 | 0.39343 | 1.26 |  | 0 | 1.995 | 0.65572 | 2.1
|  |  | AC-124 | Air-conditioning exterior unit |  |  | IM-4P | 3.58 | 1 |  |  |  | 85 | 73 | 100 | 4.2118 |  |  | 0.6 | 2.5271 | 2.3659 | 3.4617 |  | 2.3659 | 4.2118 | 3.9432 | 5.7695
|  |  | AC-159 | Air-conditioning exterior unit |  |  | IM-4P | 2.68 | 1 |  |  |  | 80 | 70 | 100 | 3.35 |  |  | 0.6 | 2.01 | 2.0506 | 2.8714 |  | 2.0506 | 3.35 | 3.4177 | 4.7857
|  |  | AC-105 | Air-conditioning exterior unit |  |  | IM-4P | 15.3 | 1 |  |  |  | 85 | 80 | 100 | 18 |  |  | 0.6 | 10.8 | 8.1 | 13.5 |  | 8.1 | 18 | 13.5 | 22.5
|  |  | AC-102 | Air-conditioning exterior unit |  |  | IM-4P | 1.6 | 1 |  |  |  | 80 | 70 | 100 | 2 |  |  | 0.6 | 1.2 | 1.2242 | 1.7143 |  | 1.2242 | 2 | 2.0404 | 2.8571
|  |  | EH-102 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 1.4 | 95 | 0.6 | 0.798 | 0.26229 | 0.84 |  | 0 | 1.33 | 0.43715 | 1.4
|  |  | AC-125 | Air-conditioning exterior unit |  |  | IM-4P | 2.5 | 1 |  |  |  | 80 | 70 | 100 | 3.125 |  |  | 0.6 | 1.875 | 1.9129 | 2.6786 |  | 1.9129 | 3.125 | 3.1881 | 4.4643
|  |  | EH-125 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 2.1 | 95 | 0.6 | 1.197 | 0.39343 | 1.26 |  | 0 | 1.995 | 0.65572 | 2.1
|  |  | AC-103 | Air-conditioning exterior unit |  |  | IM-4P | 1.6 | 1 |  |  |  | 80 | 70 | 100 | 2 |  |  | 0.6 | 1.2 | 1.2242 | 1.7143 |  | 1.2242 | 2 | 2.0404 | 2.8571
|  |  | EH-103 | ditto Booster heater |  |  | hearter | [9 empty] | 1.4 | 95 | 0.6 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
0
0
0
0
84P2 | #3P-R1 |  | AC-106 | Air-conditioning exterior unit |  |  | IM-4P | 1.6 | 1 |  |  |  | 80 | 70 | 100 | 2 |  |  | 0.6 | 1.2 | 1.2242 | 1.7143 |  | 1.2242 | 2 | 2.0404 | 2.8571
| #3 BLDG roof |  | EH-106 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 1.4 | 95 | 0.6 | 0.798 | 0.26229 | 0.84 |  | 0 | 1.33 | 0.43715 | 1.4
|  |  | AC-137-1 | Air-conditioning exterior unit |  |  | IM-4P | 1.52 | 1 |  |  |  | 80 | 70 | 100 | 1.9 |  |  | 0.6 | 1.14 | 1.163 | 1.6286 |  | 1.163 | 1.9 | 1.9384 | 2.7143
|  |  | AC-137-2 | Air-conditioning exterior unit |  |  | IM-4P | 1.52 | 1 |  |  |  | 80 | 70 | 100 | 1.9 |  |  | 0.6 | 1.14 | 1.163 | 1.6286 |  | 1.163 | 1.9 | 1.9384 | 2.7143
|  |  | AC-137-3 | Air-conditioning exterior unit |  |  | IM-4P | 1.52 | 1 |  |  |  | 80 | 70 | 100 | 1.9 |  |  | 0.6 | 1.14 | 1.163 | 1.6286 |  | 1.163 | 1.9 | 1.9384 | 2.7143
|  |  | AC-137-4 | Air-conditioning exterior unit |  |  | IM-4P | 1.52 | 1 |  |  |  | 80 | 70 | 100 | 1.9 |  |  | 0.6 | 1.14 | 1.163 | 1.6286 |  | 1.163 | 1.9 | 1.9384 | 2.7143
|  |  | AC-161 | Air-conditioning exterior unit |  |  | IM-4P | 4.52 | 1 |  |  |  | 85 | 73 | 100 | 5.3176 |  |  | 0.6 | 3.1906 | 2.9871 | 4.3707 |  | 2.9871 | 5.3176 | 4.9785 | 7.2844
|  |  | AC-126 | Air-conditioning exterior unit |  |  | IM-4P | 2.79 | 1 |  |  |  | 80 | 70 | 100 | 3.4875 |  |  | 0.6 | 2.0925 | 2.1348 | 2.9893 |  | 2.1348 | 3.4875 | 3.558 | 4.9821
|  |  | AC-129 | Air-conditioning exterior unit |  |  | IM-4P | 3.67 | 1 |  |  |  | 85 | 73 | 100 | 4.3176 |  |  | 0.6 | 2.5906 | 2.4254 | 3.5488 |  | 2.4254 | 4.3176 | 4.0423 | 5.9146
|  |  | EH-129 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 2.1 | 95 | 0.6 | 1.197 | 0.39343 | 1.26 |  | 0 | 1.995 | 0.65572 | 2.1
|  |  | AC-130 | Air-conditioning exterior unit |  |  | IM-4P | 3.5 | 1 |  |  |  | 85 | 73 | 100 | 4.1176 |  |  | 0.6 | 2.4706 | 2.313 | 3.3844 |  | 2.313 | 4.1176 | 3.8551 | 5.6406
|  |  | EH-130 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 2.1 | 95 | 0.6 | 1.197 | 0.39343 | 1.26 |  | 0 | 1.995 | 0.65572 | 2.1
|  |  | AC-123 | Air-conditioning exterior unit |  |  | IM-4P | 9.3 | 1 |  |  |  | 85 | 80 | 100 | 10.9412 |  |  | 0.6 | 6.5647 | 4.9235 | 8.2059 |  | 4.9235 | 10.9412 | 8.2059 | 13.6765
|  |  | EH-123 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 7 | 95 | 0.6 | 3.99 | 1.3114 | 4.2 |  | 0 | 6.65 | 2.1857 | 7
|  |  | AC-145-1 | Air-conditioning exterior unit |  |  | IM-4P | 17.48 | 1 |  |  |  | 85 | 80 | 100 | 20.5647 |  |  | 0.6 | 12.3388 | 9.2541 | 15.4235 |  | 9.2541 | 20.5647 | 15.4235 | 25.7059
0
0
0
0
0
0
84P3 | #3P-R2 |  | AC-145 | Air-conditioning exterior unit |  |  | IM-4P | 17.48 | 1 |  |  |  | 85 | 80 | 100 | 20.5647 |  |  | 0.6 | 12.3388 | 9.2541 | 15.4235 |  | 9.2541 | 20.5647 | 15.4235 | 25.7059
| #3 BLDG roof |  | AC-162 | Air-conditioning exterior unit |  |  | IM-4P | 1.32 | 1 |  |  |  | 80 | 70 | 100 | 1.65 |  |  | 0.6 | 0.99 | 1.01 | 1.4143 |  | 1.01 | 1.65 | 1.6833 | 2.3571
|  |  | AC-164 | Air-conditioning exterior unit |  |  | IM-4P | 2.67 | 1 |  |  |  | 80 | 70 | 100 | 3.3375 |  |  | 0.6 | 2.0025 | 2.043 | 2.8607 |  | 2.043 | 3.3375 | 3.4049 | 4.7679
|  |  | AC-138-1 | Air-conditioning exterior unit |  |  | IM-4P | 1.5 | 1 |  |  |  | 80 | 70 | 100 | 1.875 |  |  | 0.6 | 1.125 | 1.1477 | 1.6071 |  | 1.1477 | 1.875 | 1.9129 | 2.6786
|  |  | EH-138-1 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 1.7 | 95 | 0.6 | 0.969 | 0.31849 | 1.02 |  | 0 | 1.615 | 0.53082 | 1.7
|  |  | AC-138-2 | Air-conditioning exterior unit |  |  | IM-4P | 1.5 | 1 |  |  |  | 80 | 70 | 100 | 1.875 |  |  | 0.6 | 1.125 | 1.1477 | 1.6071 |  | 1.1477 | 1.875 | 1.9129 | 2.6786
|  |  | EH-138-2 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 1.7 | 95 | 0.6 | 0.969 | 0.31849 | 1.02 |  | 0 | 1.615 | 0.53082 | 1.7
|  |  | AC-117 | Air-conditioning exterior unit |  |  | IM-4P | 1.84 | 1 |  |  |  | 80 | 70 | 100 | 2.3 |  |  | 0.6 | 1.38 | 1.4079 | 1.9714 |  | 1.4079 | 2.3 | 2.3465 | 3.2857
|  |  | AC-132 | Air-conditioning exterior unit |  |  | IM-4P | 4.65 | 1 |  |  |  | 85 | 73 | 100 | 5.4706 |  |  | 0.6 | 3.2824 | 3.073 | 4.4964 |  | 3.073 | 5.4706 | 5.1217 | 7.494
|  |  | AC-160-1 | Air-conditioning exterior unit |  |  | IM-4P | 2.68 | 1 |  |  |  | 80 | 70 | 100 | 3.35 |  |  | 0.6 | 2.01 | 2.0506 | 2.8714 |  | 2.0506 | 3.35 | 3.4177 | 4.7857
|  |  | AC-160-2 | Air-conditioning exterior unit |  |  | IM-4P | 2.68 | 1 |  |  |  | 80 | 70 | 100 | 3.35 |  |  | 0.6 | 2.01 | 2.0506 | 2.8714 |  | 2.0506 | 3.35 | 3.4177 | 4.7857
|  |  | AC-141 | Air-conditioning exterior unit |  |  | IM-4P | 2.48 | 1 |  |  |  | 80 | 70 | 100 | 3.1 |  |  | 0.6 | 1.86 | 1.8976 | 2.6571 |  | 1.8976 | 3.1 | 3.1626 | 4.4286
|  |  | AC-131 | Air-conditioning exterior unit |  |  | IM-4P | 2.69 | 1 |  |  |  | 80 | 70 | 100 | 3.3625 |  |  | 0.6 | 2.0175 | 2.0583 | 2.8821 |  | 2.0583 | 3.3625 | 3.4304 | 4.8036
|  |  | AC-134-1 | Air-conditioning exterior unit |  |  | IM-4P | 1.56 | 1 |  |  |  | 80 | 70 | 100 | 1.95 |  |  | 0.6 | 1.17 | 1.1936 | 1.6714 |  | 1.1936 | 1.95 | 1.9894 | 2.7857
|  |  | AC-134-2 | Air-conditioning exterior unit |  |  | IM-4P | 1.56 | 1 |  |  |  | 80 | 70 | 100 | 1.95 |  |  | 0.6 | 1.17 | 1.1936 | 1.6714 |  | 1.1936 | 1.95 | 1.9894 | 2.7857
|  |  | AC-140 | Air-conditioning exterior unit |  |  | IM-4P | 1.52 | 1 |  |  |  | 80 | 70 | 100 | 1.9 |  |  | 0.6 | 1.14 | 1.163 | 1.6286 |  | 1.163 | 1.9 | 1.9384 | 2.7143
|  |  | EH-140 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 1.6 | 95 | 0.6 | 0.912 | 0.29976 | 0.96 |  | 0 | 1.52 | 0.4996 | 1.6
|  |  | AC-137 | Air-conditioning exterior unit |  |  | IM-4P | 1.52 | 1 |  |  |  | 80 | 70 | 100 | 1.9 |  |  | 0.6 | 1.14 | 1.163 | 1.6286 |  | 1.163 | 1.9 | 1.9384 | 2.7143
|  |  | AC-163 | Air-conditioning exterior unit |  |  | IM-4P | 4.34 | 1 |  |  |  | 85 | 73 | 100 | 5.1059 |  |  | 0.6 | 3.0635 | 2.8682 | 4.1966 |  | 2.8682 | 5.1059 | 4.7803 | 6.9944
|  |  | AC-133 | Air-conditioning exterior unit |  |  | IM-4P | 1.56 | 1 |  |  |  | 80 | 70 | 100 | 1.95 |  |  | 0.6 | 1.17 | 1.1936 | 1.6714 |  | 1.1936 | 1.95 | 1.9894 | 2.7857
|  |  | AC-119 | Air-conditioning exterior unit |  |  | IM-4P | 6.82 | 1 |  |  |  | 85 | 73 | 100 | 8.0235 |  |  | 0.6 | 4.8141 | 4.5071 | 6.5947 |  | 4.5071 | 8.0235 | 7.5119 | 10.9911
|  |  | EH-119 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 4.21 | 95 | 0.6 | 2.3997 | 0.78874 | 2.526 |  | 0 | 3.9995 | 1.3146 | 4.21
|  |  | AC-154 | Air-conditioning exterior unit |  |  | IM-4P | 3.44 | 1 |  |  |  | 80 | 70 | 100 | 4.3 |  |  | 0.6 | 2.58 | 2.6321 | 3.6857 |  | 2.6321 | 4.3 | 4.3869 | 6.1429
|  |  | AC-157 | Air-conditioning exterior unit |  |  | IM-4P | 4.52 | 1 |  |  |  | 85 | 73 | 100 | 5.3176 |  |  | 0.6 | 3.1906 | 2.9871 | 4.3707 |  | 2.9871 | 5.3176 | 4.9785 | 7.2844
0
0
0
0
0
84P4 | #4P-1 |  | AC-108 | Air-conditioning exterior unit |  |  | IM-4P | 4.67 | 1 |  |  |  | 85 | 73 | 100 | 5.4941 |  |  | 0.6 | 3.2965 | 3.0863 | 4.5157 |  | 3.0863 | 5.4941 | 5.1438 | 7.5262
| Meter R/M |  | AC-003 | Air-conditioning exterior unit |  |  | IM-4P | 10 | 1 |  |  |  | 85 | 80 | 100 | 11.7647 |  |  | 0.6 | 7.0588 | 5.2941 | 8.8235 |  | 5.2941 | 11.7647 | 8.8235 | 14.7059
|  |  | AC-142 | Air-conditioning exterior unit |  |  | IM-4P | 4.94 | 1 |  |  |  | 85 | 73 | 100 | 5.8118 |  |  | 0.6 | 3.4871 | 3.2647 | 4.7768 |  | 3.2647 | 5.8118 | 5.4411 | 7.9613
|  |  | AC-168 | Air-conditioning exterior unit |  |  | IM-4P | 1.6 | 1 |  |  |  | 80 | 70 | 100 | 2 |  |  | 0.6 | 1.2 | 1.2242 | 1.7143 |  | 1.2242 | 2 | 2.0404 | 2.8571
|  |  | AC-166-1 | Air-conditioning exterior unit |  |  | IM-4P | 2.48 | 1 |  |  |  | 80 | 70 | 100 | 3.1 |  |  | 0.6 | 1.86 | 1.8976 | 2.6571 |  | 1.8976 | 3.1 | 3.1626 | 4.4286
|  |  | AC-166-2 | Air-conditioning exterior unit |  |  | IM-4P | 2.48 | 1 |  |  |  | 80 | 70 | 100 | 3.1 |  |  | 0.6 | 1.86 | 1.8976 | 2.6571 |  | 1.8976 | 3.1 | 3.1626 | 4.4286
|  |  | AC-144 | Air-conditioning exterior unit |  |  | IM-4P | 2.57 | 1 |  |  |  | 80 | 70 | 100 | 3.2125 |  |  | 0.6 | 1.9275 | 1.9664 | 2.7536 |  | 1.9664 | 3.2125 | 3.2774 | 4.5893
|  |  | EH-144 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 2.1 | 95 | 0.6 | 1.197 | 0.39343 | 1.26 |  | 0 | 1.995 | 0.65572 | 2.1
|  |  | 4SS-1 | Electric shutter |  |  | IM-4P | 0.4 | 1 | 75.9818 | 65.8273 | 68.1818 |  |  |  | 0.35894 |  |  | 0.05 | 0.017947 | 0.020523 | 0.027264 |  | 0.020523 | 0.35894 | 0.41047 | 0.54527
|  |  | 4SS-2 | Electric shutter |  |  | IM-4P | 0.4 | 1 | 75.9818 | 65.8273 | 68.1818 |  |  |  | 0.35894 |  |  | 0.05 | 0.017947 | 0.020523 | 0.027264 |  | 0.020523 | 0.35894 | 0.41047 | 0.54527
|  |  | 4SS-3 | Electric shutter |  |  | IM-4P | 0.4 | 1 | 75.9818 | 65.8273 | 68.1818 |  |  |  | 0.35894 |  |  | 0.05 | 0.017947 | 0.020523 | 0.027264 |  | 0.020523 | 0.35894 | 0.41047 | 0.54527
0
0
0
0
0
84P5 | side board |  | R-1 | Compressor (Heat pump package A/C) |  |  | IM-4P | 30 | 2 | 92.9242 | 80.0121 |  |  |  | 110 | 71.0256 |  |  | 0.6 | 42.6154 | 31.9481 | 53.2611 | Star delta starting | 31.9481 | 71.0256 | 53.2468 | 88.7685
| #4 BLDG roof |  |  | Cooling fan |  |  | IM-4P | 0.5 | 8 |  |  |  | 75 | 65 | 80 | 4.2667 |  |  | 0.6 | 2.56 | 2.993 | 3.9385 |  | 2.993 | 4.2667 | 4.9883 | 6.5641
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
84P6 | side board |  | R-5 | Compressor (Heat pump package A/C) |  |  | IM-4P | 30 | 2 | 92.9242 | 80.0121 |  |  |  | 110 | 71.0256 |  |  | 0.6 | 42.6154 | 31.9481 | 53.2611 | Star delta starting | 31.9481 | 71.0256 | 53.2468 | 88.7685
| #4 BLDG roof |  |  | Cooling fan |  |  | IM-4P | 0.5 | 8 |  |  |  | 75 | 65 | 80 | 4.2667 |  |  | 0.6 | 2.56 | 2.993 | 3.9385 |  | 2.993 | 4.2667 | 4.9883 | 6.5641
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
84P7 | #4P-2 |  | AHU-2-1 | Supply fan of Air-conditioning M/C |  |  | IM-4P | 18.5 | 1 | 92.8 | 78.1251 | 82.3096 |  |  |  | 16.4087 |  |  | 0.6 | 9.8452 | 7.8663 | 12.6019 | Star delta starting | 7.8663 | 16.4087 | 13.1105 | 21.0031
| AC-M/C-R/M |  | AHU-2-2 | Supply fan of Air-conditioning M/C |  |  | IM-4P | 18.5 | 1 | 92.8 | 78.1251 | 82.3096 |  |  |  | 16.4087 |  |  | 0.6 | 9.8452 | 7.8663 | 12.6019 | Star delta starting | 7.8663 | 16.4087 | 13.1105 | 21.0031
|  |  | AHU-1-1 | Supply fan of Air-conditioning M/C |  |  | IM-4P | 15 | 1 | 92.2697 | 78.3788 | 78.7879 |  |  |  | 12.8083 |  |  | 0.6 | 7.685 | 6.0891 | 9.8049 | Star delta starting | 6.0891 | 12.8083 | 10.1486 | 16.3415
|  |  | AHU-1-2 | Supply fan of Air-conditioning M/C |  |  | IM-4P | 15 | 1 | 92.2697 | 78.3788 | 78.7879 |  |  |  | 12.8083 |  |  | 0.6 | 7.685 | 6.0891 | 9.8049 | Star delta starting | 6.0891 | 12.8083 | 10.1486 | 16.3415
|  |  | P-1-1 | Cooling-water circulation pump |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.6 | 1.8487 | 1.7567 | 2.5502 |  | 1.7567 | 3.0811 | 2.9278 | 4.2504
|  |  | P-1-2 | Cooling-water circulation pump |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.6 | 1.8487 | 1.7567 | 2.5502 |  | 1.7567 | 3.0811 | 2.9278 | 4.2504
|  |  | EF-5-1 | Exhaust fan |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.6 | 1.8487 | 1.7567 | 2.5502 |  | 1.7567 | 3.0811 | 2.9278 | 4.2504
|  |  | EF-5-2 | Exhaust fan |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.6 | 1.8487 | 1.7567 | 2.5502 |  | 1.7567 | 3.0811 | 2.9278 | 4.2504
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
84P8 | #5P-2 |  | AC-111 | Air-conditioning exterior unit |  |  | IM-4P | 4.27 | 1 |  |  |  | 85 | 73 | 100 | 5.0235 |  |  | 0.6 | 3.0141 | 2.8219 | 4.1289 |  | 2.8219 | 5.0235 | 4.7032 | 6.8815
| #5 BLDG roof |  | AC-002 | Air-conditioning exterior unit |  |  | IM-4P | 1.75 | 1 |  |  |  | 80 | 70 | 100 | 2.1875 |  |  | 0.6 | 1.3125 | 1.339 | 1.875 |  | 1.339 | 2.1875 | 2.2317 | 3.125
|  |  | AC-136 | Air-conditioning exterior unit |  |  | IM-4P | 1.56 | 1 |  |  |  | 80 | 70 | 100 | 1.95 |  |  | 0.6 | 1.17 | 1.1936 | 1.6714 |  | 1.1936 | 1.95 | 1.9894 | 2.7857
|  |  | AC-135 | Air-conditioning exterior unit |  |  | IM-4P | 9.28 | 1 |  |  |  | 85 | 80 | 100 | 10.9176 |  |  | 0.6 | 6.5506 | 4.9129 | 8.1882 |  | 4.9129 | 10.9176 | 8.1882 | 13.6471
|  |  | AC-152 | Air-conditioning exterior unit |  |  | IM-4P | 6.65 | 1 |  |  |  | 85 | 73 | 100 | 7.8235 |  |  | 0.6 | 4.6941 | 4.3948 | 6.4303 |  | 4.3948 | 7.8235 | 7.3246 | 10.7172
|  |  | AC-156 | Air-conditioning exterior unit |  |  | IM-4P | 5 | 1 |  |  |  | 85 | 73 | 100 | 5.8824 |  |  | 0.6 | 3.5294 | 3.3043 | 4.8348 |  | 3.3043 | 5.8824 | 5.5072 | 8.058
|  |  | EH-156 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 3.5 | 95 | 0.6 | 1.995 | 0.65572 | 2.1 |  | 0 | 3.325 | 1.0929 | 3.5
|  |  | B-65 | Air-conditioning exterior unit |  |  | IM-4P | 3.7 | 1 |  |  |  | 85 | 73 | 100 | 4.3529 |  |  | 0.6 | 2.6118 | 2.4452 | 3.5778 |  | 2.4452 | 4.3529 | 4.0753 | 5.9629
|  |  | ----- | Automatic control power supply |  |  | others |  | 1 | [7 empty] | 2 | 80 | 0.6 | 0.96 | 0.72 | 1.2 |  | 0 | 1.6 | 1.2 | 2
0
0
0
0
0
84P9 | #5 Existing |  |  | Air-conditioning apparatus sum total |  |  | IM | 96.95 | 1 |  |  |  | 82.5 | 78 | 100 | 117.5152 |  |  | 0.6 | 70.5091 | 56.5681 | 90.3963 |  | 56.5681 | 117.5152 | 94.2802 | 150.6605
| AC-M/C-R/M |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F01 |  | 3φ3W | 50 | All loads [KW] | 232 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 8 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 174 | TR. Load factor [％] |  |  | 67.6667 | TR. Load factor [％] |  |  | 67.6667 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 210 | All loads [KVA] | 290 | Demand [KW] |  |  | 162.4 | Demand [KW] |  |  | 162.4 | Capacitor
Move (TG) |  | 8-5 |  | 300 |  | Installation place | Outdoors | Demand [KVar] |  |  | 121.8 | Demand [KVar] |  |  | 121.8 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 203 | Demand [KVA] |  |  | 203 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.8 | Ave.Power factor |  |  | 0.8 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
85P1 | Dstb. Board |  |  | CHDY Analysis meter |  |  | others |  | 1 | [7 empty] | 270 | 80 | 0.7 | 151.2 | 113.4 | 189 |  | 0 | 216 | 162 | 270
| #4 meter R/M |  |  | Distribution board | [19 empty] | 0
0
0
0
0
0
85P2 | Dstb. Board |  |  | CVT equipment (3φ3W-200V) |  |  | others |  | 1 | [7 empty] | 10 | 80 | 0.7 | 5.6 | 4.2 | 7 |  | 0 | 8 | 6 | 10
| #4 meter R/M |  |  | CVT equipment (1φ2W-200V) |  |  | others |  | 1 | [7 empty] | 10 | 80 | 0.7 | 5.6 | 4.2 | 7 |  | 0 | 8 | 6 | 10
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F09 |  | 3φ3W | 50 | All loads [KW] | 558.3413 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 8 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 431.72 | TR. Load factor [％] |  |  | 57.3165 | TR. Load factor [％] |  |  | 57.3165 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 210 | All loads [KVA] | 707.9779 | Demand [KW] |  |  | 226.6529 | Demand [KW] |  |  | 226.6529 | Capacitor
Existing |  | 8-2 |  | 500 |  | Installation place | in boad | Demand [KVar] |  |  | 175.3795 | Demand [KVar] |  |  | 175.3795 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 286.5824 | Demand [KVA] |  |  | 286.5824 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | (F)-molded |  | Ave.Power factor |  |  | 0.79088 | Ave.Power factor |  |  | 0.79088 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
82P1-01 | #3P-11 |  | G2-9 | Throwing in Heater for (G2-8) |  |  | hearter |  | 1 | [7 empty] | 11 | 95 | 0.4 | 4.18 | 1.3739 | 4.4 |  | 0 | 10.45 | 3.4347 | 11
| R/M-102 |  | G2-7 | Cooling tower fan |  |  | IM-4P | 2.2 | 1 | 86.6653 | 72.1992 | 76.4463 |  |  |  | 1.9406 |  |  | 0.6 | 1.1644 | 1.1158 | 1.6127 |  | 1.1158 | 1.9406 | 1.8597 | 2.6878
|  |  |  | Cooling-water circulation pump |  |  | IM-4P | 3.7 | 1 | 87.0396 | 72.4912 | 72.4816 |  |  |  | 3.0811 |  |  | 0.6 | 1.8487 | 1.7567 | 2.5502 |  | 1.7567 | 3.0811 | 2.9278 | 4.2504
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
82P-02 | #3P-12 |  | G2-13 | Controller unit for (G2-12) |  |  | others |  | 1 | [7 empty] | 52 | 80 | 0.4 | 16.64 | 12.48 | 20.8 |  | 0 | 41.6 | 31.2 | 52
| 103 |  | ATF-09 | CVT tester (Oil pressure circuit-1) |  |  | others |  | 1 | [7 empty] | 11 | 80 | 0.4 | 3.52 | 2.64 | 4.4 |  | 0 | 8.8 | 6.6 | 11
|  |  | ATF-10 | CVT tester (Oil pressure circuit-2) |  |  | others |  | 1 | [7 empty] | 1.4 | 80 | 0.4 | 0.448 | 0.336 | 0.56 |  | 0 | 1.12 | 0.84 | 1.4
|  |  | ATF-56 | Shudder demonstration tester |  |  | others |  | 1 | [7 empty] | 18 | 80 | 0.4 | 5.76 | 4.32 | 7.2 |  | 0 | 14.4 | 10.8 | 18
|  |  | ATF-57 | Rapid precision cutter |  |  | others |  | 1 | [7 empty] | 2.8 | 80 | 0.4 | 0.896 | 0.672 | 1.12 |  | 0 | 2.24 | 1.68 | 2.8
|  |  |  | Wall socket |  |  | others |  | 1 | [7 empty] | 1 | 60 | 0.4 | 0.24 | 0.32 | 0.4 |  | 0 | 0.6 | 0.8 | 1
0
0
0
0
0
82P1-03 | #3P-13 |  | ATF-15 | Control board (No.2 UV tester) |  |  | others |  | 1 | [7 empty] | 18 | 80 | 0.4 | 5.76 | 4.32 | 7.2 |  | 0 | 14.4 | 10.8 | 18
| 105･106 |  | ATF-19 | Control board (No.3 UV tester) |  |  | others |  | 1 | [7 empty] | 18 | 80 | 0.4 | 5.76 | 4.32 | 7.2 |  | 0 | 14.4 | 10.8 | 18
|  |  | ATF-24 | Draft chamber (UV tester) |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  |  | SD tester |  |  | IM-4P | 0.4 | 1 | 75.9818 | 65.8273 | 68.1818 |  |  |  | 0.35894 |  |  | 0.4 | 0.14358 | 0.16419 | 0.21811 |  | 0.16419 | 0.35894 | 0.41047 | 0.54527
|  |  |  | Wall socket (test prototype machine) |  |  | others |  | 8 | [7 empty] | 1 | 60 | 0.4 | 1.92 | 2.56 | 3.2 |  | 0 | 4.8 | 6.4 | 8
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
82P2-01 | #3P-14 |  | G3-2 | 4-roller tractiomn tester-1 |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 0.4 | 0.16 | 0.12 | 0.2 |  | 0 | 0.4 | 0.3 | 0.5
| 107 |  | G3-3 | 4-roller tractiomn tester-2 |  |  | others |  | 1 | [7 empty] | 14 | 80 | 0.4 | 4.48 | 3.36 | 5.6 |  | 0 | 11.2 | 8.4 | 14
|  |  | G3-5 | 4-roller tractiomn tester-3 |  |  | others |  | 1 | [7 empty] | 35 | 80 | 0.4 | 11.2 | 8.4 | 14 |  | 0 | 28 | 21 | 35
|  |  | G3-8 | 4-roller tractiomn tester-4 |  |  | others |  | 1 | [7 empty] | 26 | 80 | 0.4 | 8.32 | 6.24 | 10.4 |  | 0 | 20.8 | 15.6 | 26
0
0
0
82P2-02 | #3P-15 |  | G1-9 | Synchromesh durability test stand-1 |  |  | others |  | 1 | [7 empty] | 9 | 80 | 0.4 | 2.88 | 2.16 | 3.6 |  | 0 | 7.2 | 5.4 | 9
| 108 | [22 empty] | 0
0
0
0
0
82P2-03 | #3P-16 |  | G2-17 | Bowden tester |  |  | others |  | 1 | [7 empty] | 11 | 80 | 0.4 | 3.52 | 2.64 | 4.4 |  | 0 | 8.8 | 6.6 | 11
| 111･112 |  | D-36 | Draft chamber (washing) |  |  | others |  | 1 | [7 empty] | 3.5 | 80 | 0.4 | 1.12 | 0.84 | 1.4 |  | 0 | 2.8 | 2.1 | 3.5
|  |  | E-29 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  |  | Draft chamber (for B-50) |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
82P2-04 | #3P-17 |  | ATF-59 | Hoop centering tester |  |  | others |  | 1 | [7 empty] | 18 | 80 | 0.4 | 5.76 | 4.32 | 7.2 |  | 0 | 14.4 | 10.8 | 18
| 114 |  | ATF-61 | LFW-1 (No.1) |  |  | others |  | 1 | [7 empty] | 2.6 | 80 | 0.4 | 0.832 | 0.624 | 1.04 |  | 0 | 2.08 | 1.56 | 2.6
|  |  | ATF-65 | LFW-1 (No.2) |  |  | others |  | 1 | [7 empty] | 2.6 | 80 | 0.4 | 0.832 | 0.624 | 1.04 |  | 0 | 2.08 | 1.56 | 2.6
|  |  | ATF-69 | Draft chamber |  |  | others |  | 1 | [7 empty] | 1.4 | 80 | 0.4 | 0.448 | 0.336 | 0.56 |  | 0 | 1.12 | 0.84 | 1.4
|  |  | ATF-71 | SRV tester (No.3) |  |  | others |  | 1 | [7 empty] | 4.5 | 80 | 0.4 | 1.44 | 1.08 | 1.8 |  | 0 | 3.6 | 2.7 | 4.5
|  |  | D-9 | SRV weartester |  |  | others |  | 1 | [7 empty] | 7 | 80 | 0.4 | 2.24 | 1.68 | 2.8 |  | 0 | 5.6 | 4.2 | 7
|  |  | E-30 | 4-ball test M/C |  |  | others |  | 1 | [7 empty] | 1.8 | 80 | 0.4 | 0.576 | 0.432 | 0.72 |  | 0 | 1.44 | 1.08 | 1.8
|  |  | S-33 | Friction wear examination machine |  |  | others |  | 1 | [7 empty] | 9 | 80 | 0.4 | 2.88 | 2.16 | 3.6 |  | 0 | 7.2 | 5.4 | 9
|  |  |  | Wall socket (test prototype machine) |  |  | others |  | 2 | [7 empty] | 1 | 60 | 0.4 | 0.48 | 0.64 | 0.8 |  | 0 | 1.2 | 1.6 | 2
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
82P2-05 | #3P-18 |  | G3-34 | Vacuum pump (for driers) |  |  | IM-4P | 0.4 | 1 | 75.9818 | 65.8273 | 68.1818 |  |  |  | 0.35894 |  |  | 0.4 | 0.14358 | 0.16419 | 0.21811 |  | 0.16419 | 0.35894 | 0.41047 | 0.54527
| 115 |  | G3-41 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
82P2-06 | Control board |  | ELV-1 | Elevator |  |  | IM |  | 1 | [7 empty] | 4.6 | 80 | 0.05 | 0.184 | 0.138 | 0.23 |  | 0 | 3.68 | 2.76 | 4.6
| ELV. | [22 empty] | 0
0
0
0
0
82P3-01 | #3P-21 |  | S-2 | Auto. non-dissolved analysis tester |  |  | others |  | 1 | [7 empty] | 7.5 | 80 | 0.4 | 2.4 | 1.8 | 3 |  | 0 | 6 | 4.5 | 7.5
| 201 |  | S-48 | Drier |  |  | others |  | 1 | [7 empty] | 2.5 | 80 | 0.4 | 0.8 | 0.6 | 1 |  | 0 | 2 | 1.5 | 2.5
|  |  |  | Draft chamber (for S-2) |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | S-120 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
0
0
0
0
82P3-02 | #3P-24 |  | S-41 | BF tub (coefficient of viscosity) |  |  | others |  | 1 | [7 empty] | 6 | 80 | 0.4 | 1.92 | 1.44 | 2.4 |  | 0 | 4.8 | 3.6 | 6
| 204 |  | S-42 | BF tub (coefficient of viscosity) |  |  | others |  | 1 | [7 empty] | 2 | 80 | 0.4 | 0.64 | 0.48 | 0.8 |  | 0 | 1.6 | 1.2 | 2
|  |  | S-43 | BF tub (coefficient of viscosity) |  |  | others |  | 1 | [7 empty] | 2 | 80 | 0.4 | 0.64 | 0.48 | 0.8 |  | 0 | 1.6 | 1.2 | 2
|  |  | S-44 | BF tub (coefficient of viscosity) |  |  | others |  | 1 | [7 empty] | 2 | 80 | 0.4 | 0.64 | 0.48 | 0.8 |  | 0 | 1.6 | 1.2 | 2
|  |  | S-112 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
| #3P-23 |  | D-12 | 2-cylinder traction tester |  |  |  |  | 1 | [7 empty] | 3.8 | 80 | 0.4 | 1.216 | 0.912 | 1.52 |  | 0 | 3.04 | 2.28 | 3.8
| 203 |  | E-58 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
| #3P-22 |  | D-35 | Experimental equipment with draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
| 202 |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
82P3-03 | #3P-25 |  | D-11 | Refrigerator |  |  | IM |  | 1 | [7 empty] | 8 | 80 | 0.4 | 2.56 | 1.92 | 3.2 |  | 0 | 6.4 | 4.8 | 8
| 205･206 |  | S-106 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
| #3P-26 |  | S-105 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
| 207 |  | S-35 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | S-140 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
82P3-04 | #3P-27 |  | S-49 | Drier (with compulsive ventilation) |  |  | others |  | 1 | [7 empty] | 3.5 | 80 | 0.4 | 1.12 | 0.84 | 1.4 |  | 0 | 2.8 | 2.1 | 3.5
| 209 |  | S-34 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | S-29 | Turbine oil oxidization stability tester |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
0
82P3-05 | #3P-28 |  | S-58,59 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
| 210 |  | G3-24 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
82P3-06 | #3P-29 |  | S-21 | Lubricating oil tester |  |  | others |  | 1 | [7 empty] | 7.7 | 80 | 0.4 | 2.464 | 1.848 | 3.08 |  | 0 | 6.16 | 4.62 | 7.7
| 211 |  | S-30 | Bath (low-temp.coefficient of viscosity) |  |  | others |  | 1 | [7 empty] | 10.4 | 80 | 0.4 | 3.328 | 2.496 | 4.16 |  | 0 | 8.32 | 6.24 | 10.4
|  |  | S-37 | Auto. pour point and cloudy point tester |  |  | others |  | 1 | [7 empty] | 10.4 | 80 | 0.4 | 3.328 | 2.496 | 4.16 |  | 0 | 8.32 | 6.24 | 10.4
|  |  | S-38 | Supersonic centrifugal separation M/C |  |  | others |  | 1 | [7 empty] | 10.4 | 80 | 0.4 | 3.328 | 2.496 | 4.16 |  | 0 | 8.32 | 6.24 | 10.4
|  |  | S-31,-82 | Wall socket (test prototype machine) |  |  | others |  | 2 | [7 empty] | 1 | 60 | 0.4 | 0.48 | 0.64 | 0.8 |  | 0 | 1.2 | 1.6 | 2
0
0
0
0
0
82P3-07 | #3P-30 |  | S-53 | Diesel inject examination machine |  |  | others |  | 1 | [7 empty] | 3.5 | 80 | 0.4 | 1.12 | 0.84 | 1.4 |  | 0 | 2.8 | 2.1 | 3.5
| 212 |  |  | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | S-110 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
| #3P-31 |  | E-55 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
| 213 |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
82P9 | #3S-29 |  | G3-13 | Control board (IAE Gear tester) |  |  | others |  | 1 | [7 empty] | 78 | 80 | 0.4 | 24.96 | 18.72 | 31.2 |  | 0 | 62.4 | 46.8 | 78
| 116 | [22 empty] | 0
0
0
0
0
82P4 | #3S-11 |  | G2-5 | Oil pressure unit (#3-R/M-102) |  |  | IM-4P |  | 1 | [7 empty] | 130 | 80 | 0.4 | 41.6 | 31.2 | 52 |  | 0 | 104 | 78 | 130
| 102 | [22 empty] | 0
0
0
0
0
82P5 | #3S-12 |  | G2-8 | VCF tester No.2 (#3-R/M-102) |  |  | others |  | 1 | [7 empty] | 70 | 80 | 0.4 | 22.4 | 16.8 | 28 |  | 0 | 56 | 42 | 70
| 102 | [22 empty] | 0
0
0
0
0
0
0
82P6 | #3S-23 |  | ATF-36 | SAE No.2 tester No.3 board |  |  | others |  | 1 | [7 empty] | 78 | 80 | 0.4 | 24.96 | 18.72 | 31.2 |  | 0 | 62.4 | 46.8 | 78
| 106 | [22 empty] | 0
0
0
0
0
82P7 | #3S-22 |  | ATF-44 | SAE No.2 tester No.4 board |  |  | others |  | 1 | [7 empty] | 78 | 80 | 0.4 | 24.96 | 18.72 | 31.2 |  | 0 | 62.4 | 46.8 | 78
| 106 | [22 empty] | 0
0
0
0
0
82P8 | #5P-1 |  | B-49 | Move formula crane |  |  | IM-4P |  | 1 | [7 empty] | 1.8 | 80 | 0.4 | 0.576 | 0.432 | 0.72 |  | 0 | 1.44 | 1.08 | 1.8
| Blend R/M(1) |  | B-01 | Basis material oil pressure supply unit |  |  | others |  | 1 | [7 empty] | 1.8 | 80 | 0.4 | 0.576 | 0.432 | 0.72 |  | 0 | 1.44 | 1.08 | 1.8
|  |  | B-33 | Heating churning M/C |  |  | IM |  | 1 | [7 empty] | 17.4 | 80 | 0.4 | 5.568 | 4.176 | 6.96 |  | 0 | 13.92 | 10.44 | 17.4
|  |  | B-32 | Heating churning M/C |  |  | IM |  | 1 | [7 empty] | 17.4 | 80 | 0.4 | 5.568 | 4.176 | 6.96 |  | 0 | 13.92 | 10.44 | 17.4
|  |  | B-31 | Heating churning M/C |  |  | IM |  | 1 | [7 empty] | 17.4 | 80 | 0.4 | 5.568 | 4.176 | 6.96 |  | 0 | 13.92 | 10.44 | 17.4
|  |  | B-30 | Heating churning M/C |  |  | IM |  | 1 | [7 empty] | 10.4 | 80 | 0.4 | 3.328 | 2.496 | 4.16 |  | 0 | 8.32 | 6.24 | 10.4
|  |  | B-29 | Heating churning M/C |  |  | IM |  | 1 | [7 empty] | 10.4 | 80 | 0.4 | 3.328 | 2.496 | 4.16 |  | 0 | 8.32 | 6.24 | 10.4
|  |  | B-40 | Additive agent dissolution equipment |  |  | others |  | 1 | [7 empty] | 7 | 80 | 0.4 | 2.24 | 1.68 | 2.8 |  | 0 | 5.6 | 4.2 | 7
|  |  |  | Additive agent dissolution equipment |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | B-35 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | B-36 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | EF- | Exhaust fan (Oil storage R/M) |  |  | IM-4P | 0.2 | 1 | 71.9545 | 65.0182 | 79.5455 |  |  |  | 0.2211 |  |  | 0.4 | 0.08844 | 0.10335 | 0.13602 |  | 0.10335 | 0.2211 | 0.25837 | 0.34006
|  |  | ----- | Operation power supply |  |  |  |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F09 |  | 3φ3W | 50 | All loads [KW] | 342.7938 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 8 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 244.7716 | TR. Load factor [％] |  |  | 49.1416 | TR. Load factor [％] |  |  | 49.1416 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 420 | All loads [KVA] | 421.9325 | Demand [KW] |  |  | 239.9557 | Demand [KW] |  |  | 239.9557 | Capacitor
Move (Saitama) |  | 8-6 |  | 600 |  | Installation place | in boad | Demand [KVar] |  |  | 171.3401 | Demand [KVar] |  |  | 171.3401 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 294.8494 | Demand [KVA] |  |  | 294.8494 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.81382 | Ave.Power factor |  |  | 0.81382 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
|  |  |  | No.1 Chassis Dynamo equipment | [19 empty] | 0
0
86P1 | No.1 CHDY |  | CHDY1 | No.1 Chassis Dynamo |  |  | others | 220 | 1 |  |  |  | 95 | 80 | 100 | 231.5789 |  |  | 0.7 | 162.1053 | 121.5789 | 202.6316 |  | 121.5789 | 231.5789 | 173.6842 | 289.4737
| Switchboard place |  | CHDY1-CF | Dynamo E/G cooling fan |  |  | IM-4P | 90 | 1 |  |  |  | 93 | 86 | 100 | 96.7742 |  |  | 0.7 | 67.7419 | 40.1957 | 78.7697 |  | 40.1957 | 96.7742 | 57.4224 | 112.5281
|  |  | CHDY1-F1 | Dynamo cooling fan-No.1 |  |  | IM-4P | 5.5 | 1 | 89.2835 | 75.881 | 76.0331 |  |  |  | 4.6838 |  |  | 0.7 | 3.2786 | 2.8142 | 4.3207 |  | 2.8142 | 4.6838 | 4.0202 | 6.1725
|  |  | CHDY1-F2 | Dynamo cooling fan-No.2 |  |  | IM-4P | 5.5 | 1 | 89.2835 | 75.881 | 76.0331 |  |  |  | 4.6838 |  |  | 0.7 | 3.2786 | 2.8142 | 4.3207 |  | 2.8142 | 4.6838 | 4.0202 | 6.1725
|  |  | CHDY1-F3 | Dynamo cooling fan-No.3 |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.7 | 0.86911 | 1.0548 | 1.3667 |  | 1.0548 | 1.2416 | 1.5068 | 1.9525
|  |  | CHDY1-M1 | Dynamo roller movement equipment |  |  | IM-4P | 2.2 | 1 | 86.6653 | 72.1992 | 76.4463 |  |  |  | 1.9406 |  |  | 0.7 | 1.3584 | 1.3018 | 1.8815 |  | 1.3018 | 1.9406 | 1.8597 | 2.6878
|  |  | CHDY1-M2 | Dynamo E/G-CF movement equipment |  |  | IM-4P | 0.75 | 1 | 80.4909 | 65.4061 | 69.697 |  |  |  | 0.64942 |  |  | 0.7 | 0.4546 | 0.52576 | 0.69504 |  | 0.52576 | 0.64942 | 0.75108 | 0.99291
|  |  | CHDY1-P1 | Dynamo lubricating oil pump-No.1 |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.7 | 0.86911 | 1.0548 | 1.3667 | 421.9[KVA](Df=1) | 1.0548 | 1.2416 | 1.5068 | 1.9525
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F09 |  | 3φ3W | 50 | All loads [KW] | 404.596 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 8 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 266.9897 | TR. Load factor [％] |  |  | 67.8948 | TR. Load factor [％] |  |  | 67.8948 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 420 | All loads [KVA] | 485.3818 | Demand [KW] |  |  | 283.3372 | Demand [KW] |  |  | 283.3372 | Capacitor
New |  | 8-7 |  | 500 |  | Installation place | in boad | Demand [KVar] |  |  | 186.9828 | Demand [KVar] |  |  | 186.9828 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 339.4739 | Demand [KVA] |  |  | 339.4739 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.83464 | Ave.Power factor |  |  | 0.83464 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
|  |  |  | CVT equipment | [19 empty] | 0
0
87P1 |  |  | CVTDY | Dynamo |  |  | others | 100 | 1 |  |  |  | 95 | 80 | 100 | 105.2632 |  |  | 0.7 | 73.6842 | 55.2632 | 92.1053 |  | 55.2632 | 105.2632 | 78.9474 | 131.5789
|  |  | CVTDY-CF | Dynamo cooling fan |  |  | IM-4P | 2.2 | 1 | 86.6653 | 72.1992 | 76.4463 |  |  |  | 1.9406 |  |  | 0.7 | 1.3584 | 1.3018 | 1.8815 |  | 1.3018 | 1.9406 | 1.8597 | 2.6878
|  |  | CVTDY-CP | Dynamo cooling water pump |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.7 | 0.86911 | 1.0548 | 1.3667 |  | 1.0548 | 1.2416 | 1.5068 | 1.9525
|  |  | CVTM-CF | Moter |  |  | others | 100 | 1 |  |  |  | 95 | 85 | 100 | 105.2632 |  |  | 0.7 | 73.6842 | 45.6654 | 86.6873 |  | 45.6654 | 105.2632 | 65.2362 | 123.839
|  |  | CVTM-CF | Moter cooling fan |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.7 | 0.86911 | 1.0548 | 1.3667 |  | 1.0548 | 1.2416 | 1.5068 | 1.9525
|  |  | CVTM-CP | Moter cooling water pump |  |  | IM-4P | 0.75 | 1 | 80.4909 | 65.4061 | 69.697 |  |  |  | 0.64942 |  |  | 0.7 | 0.4546 | 0.52576 | 0.69504 | 263[KVA](Df=1) | 0.52576 | 0.64942 | 0.75108 | 0.99291
0
0
0
0
0
87P2 | #3S-19 |  | ATF-4 | Moter |  |  | others | 100 | 1 |  |  |  | 95 | 85 | 100 | 105.2632 |  |  | 0.7 | 73.6842 | 45.6654 | 86.6873 |  | 45.6654 | 105.2632 | 65.2362 | 123.839
| R/M-103 |  | ATF-4-2 | Moter |  |  | others | 75 | 1 |  |  |  | 90 | 85 | 100 | 83.3333 |  |  | 0.7 | 58.3333 | 36.1518 | 68.6275 |  | 36.1518 | 83.3333 | 51.6454 | 98.0392
|  |  |  | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 | 155.8[KVA](Df=1) | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F07-TR60 |  | 1φ3W | 50 | All loads [KW] | 106.998 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 6 S/S |  | Prm.[V] | 420 | All loads [KVar] | 134.6256 | TR. Load factor [％] |  |  | 73.5625 | TR. Load factor [％] |  |  | 73.5625 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 210/105 | All loads [KVA] | 173.07 | Demand [KW] |  |  | 47.5332 | Demand [KW] |  |  | 47.5332 | Capacitor
Exchange |  | 6-1 |  | 100 |  | Installation place | Outdoors | Demand [KVar] |  |  | 56.143 | Demand [KVar] |  |  | 56.143 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 73.5625 | Demand [KVA] |  |  | 73.5625 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.64616 | Ave.Power factor |  |  | 0.64616 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
61L1 | #6L-1 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 0.57 | 90 | 0.9 | 0.4617 | 0.22361 | 0.513 |  | 0 | 0.513 | 0.24846 | 0.57
| Pas. |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 3.9 | 60 | 0.4 | 0.936 | 1.248 | 1.56 |  | 0 | 2.34 | 3.12 | 3.9
0
0
| #6L-2 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 1.4 | 90 | 0.9 | 1.134 | 0.54922 | 1.26 |  | 0 | 1.26 | 0.61025 | 1.4
| R/M (1)-FCC |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 19.3 | 60 | 0.4 | 4.632 | 6.176 | 7.72 |  | 0 | 11.58 | 15.44 | 19.3
0
| Catalyst | [22 empty] | 0
| #6L-4 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 0.65 | 90 | 0.9 | 0.5265 | 0.255 | 0.585 |  | 0 | 0.585 | 0.28333 | 0.65
| R/M(3)-CTLST |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 7.15 | 60 | 0.4 | 1.716 | 2.288 | 2.86 |  | 0 | 4.29 | 5.72 | 7.15
0
0
61L2 | #6L-3 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 1.2 | 90 | 0.9 | 0.972 | 0.47076 | 1.08 |  | 0 | 1.08 | 0.52307 | 1.2
| R/M (2)-HP |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 46.25 | 60 | 0.4 | 11.1 | 14.8 | 18.5 |  | 0 | 27.75 | 37 | 46.25
0
0
61L3 | #6L-5 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 1.2 | 90 | 0.9 | 0.972 | 0.47076 | 1.08 |  | 0 | 1.08 | 0.52307 | 1.2
| R/M (4)-CPRT |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 17.15 | 60 | 0.4 | 4.116 | 5.488 | 6.86 |  | 0 | 10.29 | 13.72 | 17.15
0
0
| #6L-6 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 1.4 | 90 | 0.9 | 1.134 | 0.54922 | 1.26 |  | 0 | 1.26 | 0.61025 | 1.4
| R/M(5)-Fuel-1 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 23.8 | 60 | 0.4 | 5.712 | 7.616 | 9.52 |  | 0 | 14.28 | 19.04 | 23.8
0
0
61L4 | #6L-7 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 2.1 | 90 | 0.9 | 1.701 | 0.82383 | 1.89 |  | 0 | 1.89 | 0.91537 | 2.1
| R/M(6)-Fuel-2 |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 31.8 | 60 | 0.4 | 7.632 | 10.176 | 12.72 |  | 0 | 19.08 | 25.44 | 31.8
0
0
| #6L-8 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 1.2 | 90 | 0.9 | 0.972 | 0.47076 | 1.08 |  | 0 | 1.08 | 0.52307 | 1.2
| R/M(9)-ANLS |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 12.6 | 60 | 0.4 | 3.024 | 4.032 | 5.04 |  | 0 | 7.56 | 10.08 | 12.6
0
0
61L5 | #9LP-1 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 0.8 | 90 | 0.9 | 0.648 | 0.31384 | 0.72 |  | 0 | 0.72 | 0.34871 | 0.8
|  |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 0.6 | 60 | 0.4 | 0.144 | 0.192 | 0.24 |  | 0 | 0.36 | 0.48 | 0.6
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F07-TR60 |  | 3φ3W | 50 | All loads [KW] | 159.4481 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 6 S/S |  | Prm.[V] | 420 | All loads [KVar] | 121.9037 | TR. Load factor [％] |  |  | 78.6555 | TR. Load factor [％] |  |  | 78.6555 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 210 | All loads [KVA] | 203.0658 | Demand [KW] |  |  | 93.5701 | Demand [KW] |  |  | 93.5701 | Capacitor
Existing |  | 6-2 |  | 150 |  | Installation place | Outdoors | Demand [KVar] |  |  | 71.8657 | Demand [KVar] |  |  | 71.8657 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 117.9832 | Demand [KVA] |  |  | 117.9832 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.79308 | Ave.Power factor |  |  | 0.79308 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
62P1 | #6P-3 |  | C-33 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
| R/M (4)-CPRT |  | C-35 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | C-58 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | Ana-198 | Vacuum evaporation equipment |  |  | others |  | 1 | [7 empty] | 3.8 | 80 | 0.4 | 1.216 | 0.912 | 1.52 |  | 0 | 3.04 | 2.28 | 3.8
|  |  | Ana-201 | Automatic polish M/C |  |  | IM-4P |  | 1 | [7 empty] | 1.9 | 80 | 0.4 | 0.608 | 0.456 | 0.76 |  | 0 | 1.52 | 1.14 | 1.9
|  |  | Existing | Supply fan |  |  | IM-4P | 0.4 | 2 | 75.9818 | 65.8273 | 68.1818 |  |  |  | 0.71788 |  |  | 0.8 | 0.5743 | 0.65675 | 0.87243 |  | 0.65675 | 0.71788 | 0.82094 | 1.0905
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
| #6P-1 |  | AC-104 | Air-conditioning exterior unit |  |  | IM-4P | 1.81 | 1 |  |  |  | 80 | 70 | 100 | 2.2625 |  |  | 0.8 | 1.81 | 1.8466 | 2.5857 |  | 1.8466 | 2.2625 | 2.3082 | 3.2321
| R/M (1)-FCC | [22 empty] | 0
0
0
0
0
0
| #6P-2 |  | Fuel-01 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
| R/M (2)-HP |  | C-36 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | C-77 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | C-19 | A213 electric furnace |  |  | hearter |  | 1 | [7 empty] | 15 | 95 | 0.4 | 5.7 | 1.8735 | 6 |  | 0 | 14.25 | 4.6837 | 15
|  |  | EF- | ditto local exhaust fan |  |  | IM-4P | 0.75 | 1 | 80.4909 | 65.4061 | 69.697 |  |  |  | 0.64942 |  |  | 0.4 | 0.25977 | 0.30043 | 0.39716 |  | 0.30043 | 0.64942 | 0.75108 | 0.99291
|  |  | C-07 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | EF- | Draft chamber (for C-08) |  |  | IM-4P | 0.75 | 1 | 80.4909 | 65.4061 | 69.697 |  |  |  | 0.64942 |  |  | 0.4 | 0.25977 | 0.30043 | 0.39716 |  | 0.30043 | 0.64942 | 0.75108 | 0.99291
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
62P2 | #6P-5 |  | G3-33 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
| R/M(6)-Fuel-2 |  | G3-43 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | Fuel-28 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | Existing | Draft chamber |  |  | IM-4P | 1.5 | 2 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 2.4832 |  |  | 0.4 | 0.99327 | 1.2055 | 1.562 |  | 1.2055 | 2.4832 | 3.0137 | 3.9049
|  |  | Fuel-55 | full automatic const. humidity Filter |  |  | others |  | 1 | [7 empty] | 3.8 | 80 | 0.4 | 1.216 | 0.912 | 1.52 |  | 0 | 3.04 | 2.28 | 3.8
|  |  | Fuel-20 | const. temperature tub |  |  | hearter |  | 1 | [7 empty] | 10 | 95 | 0.4 | 3.8 | 1.249 | 4 |  | 0 | 9.5 | 3.1225 | 10
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
| #6P-4 |  | Fuel-35 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
| R/M(5)-Fuel-1 |  | Fuel-36 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | Existing | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
62P3 | #6P-6 |  | Ana-164 | MMR |  |  | others |  | 1 | [7 empty] | 13.3 | 80 | 0.4 | 4.256 | 3.192 | 5.32 |  | 0 | 10.64 | 7.98 | 13.3
| R/M(9)-ANLS |  | AC-001 | Air-conditioning exterior unit |  |  | IM-4P | 6.64 | 1 |  |  |  | 85 | 73 | 100 | 7.8118 |  |  | 0.8 | 6.2494 | 5.8509 | 8.5608 |  | 5.8509 | 7.8118 | 7.3136 | 10.701
|  |  | OF-001 | Supply fan |  |  | IM-4P | 0.4 | 1 | 75.9818 | 65.8273 | 68.1818 |  |  |  | 0.35894 |  |  | 0.8 | 0.28715 | 0.32838 | 0.43622 |  | 0.32838 | 0.35894 | 0.41047 | 0.54527
|  |  | Fuel-67 | Clean R/M |  |  | others |  | 1 | [7 empty] | 24.25 | 80 | 0.4 | 7.76 | 5.82 | 9.7 |  | 0 | 19.4 | 14.55 | 24.25
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
62P4 | #9LP-1 |  |  | Power supply of building |  |  | IM-4P | 2.65 | 1 |  |  |  | 80 | 70 | 75 | 2.4844 |  |  | 0.05 | 0.12422 | 0.12673 | 0.17746 |  | 0.12673 | 2.4844 | 2.5346 | 3.5491
0
0
0
0
0
| #6 Existing |  |  | Air-conditioning apparatus sum total |  |  | IM | 50 | 1 |  |  |  | 80 | 80 | 100 | 62.5 |  |  | 0.8 | 50 | 37.5 | 62.5 |  | 37.5 | 62.5 | 46.875 | 78.125
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F03 |  | 1φ3W | 50 | All loads [KW] | 103.61 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 7 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 122.5122 | TR. Load factor [％] |  |  | 73.6784 | TR. Load factor [％] |  |  | 73.6784 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 210/105 | All loads [KVA] | 162.45 | Demand [KW] |  |  | 50.672 | Demand [KW] |  |  | 50.672 | Capacitor
Existing |  | 7-1 |  | 100 |  | Installation place | in boad | Demand [KVar] |  |  | 53.4869 | Demand [KVar] |  |  | 53.4869 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 73.6784 | Demand [KVA] |  |  | 73.6784 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.68775 | Ave.Power factor |  |  | 0.68775 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
71L1 | #7L-11 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 7.3 | 90 | 0.9 | 5.913 | 2.8638 | 6.57 |  | 0 | 6.57 | 3.182 | 7.3
| 1F-GC |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 27.2 | 60 | 0.4 | 6.528 | 8.704 | 10.88 |  | 0 | 16.32 | 21.76 | 27.2
0
0
71L2 | #7L-12 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 1.5 | 90 | 0.9 | 1.215 | 0.58845 | 1.35 |  | 0 | 1.35 | 0.65383 | 1.5
| 1F-ICP |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 20.4 | 60 | 0.4 | 4.896 | 6.528 | 8.16 |  | 0 | 12.24 | 16.32 | 20.4
0
0
71L3 | #7L-13 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 6.6 | 90 | 0.9 | 5.346 | 2.5892 | 5.94 |  | 0 | 5.94 | 2.8769 | 6.6
| 1F-XPS |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 25 | 60 | 0.4 | 6 | 8 | 10 |  | 0 | 15 | 20 | 25
0
0
71L4 | #7L-21 |  |  | Lighting load |  |  |  |  | 1 | [7 empty] | 2.2 | 90 | 0.9 | 1.782 | 0.86306 | 1.98 |  | 0 | 1.98 | 0.95896 | 2.2
| 2F-Atom |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 37.65 | 60 | 0.4 | 9.036 | 12.048 | 15.06 |  | 0 | 22.59 | 30.12 | 37.65
[7 empty] | others | [16 empty] | 0
0
71L5 | #7L-22 |  |  | Lighting load |  |  | others |  | 1 | [7 empty] | 2.8 | 90 | 0.9 | 2.268 | 1.0984 | 2.52 |  | 0 | 2.52 | 1.2205 | 2.8
| 2F-M/C-R/M |  |  | Wall socket (test prototype machine) |  |  | others |  | 1 | [7 empty] | 31.7 | 60 | 0.4 | 7.608 | 10.144 | 12.68 |  | 0 | 19.02 | 25.36 | 31.7
0
0
71L6 | CB-LGR |  |  | Low volt. ground relay power supply |  |  | others |  | 1 | [7 empty] | 0.1 | 80 | 1 | 0.08 | 0.06 | 0.1 |  | 0 | 0.08 | 0.06 | 0.1
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Prm.Group No. |  | 152-F03 |  | 3φ3W | 50 | All loads [KW] | 180.6751 | with no Capacitor |  |  |  | with Capacitor |  |  |  | Notes.Capacitor installed |  |  | Project name
Substation No. |  | 7 S/S |  | Prm.[V] | 3300 | All loads [KVar] | 233.5967 | TR. Load factor [％] |  |  | 56.8285 | TR. Load factor [％] |  |  | 56.8285 | in the secondary side. |  |  | TGCRDL Relocation Project
Sec.Group No. |  | 1 |  | Sec.[V] | 210 | All loads [KVA] | 322.8744 | Demand [KW] |  |  | 114.1971 | Demand [KW] |  |  | 114.1971 | Capacitor
New |  | 7-2 |  | 300 |  | Installation place | in boad | Demand [KVar] |  |  | 126.5873 | Demand [KVar] |  |  | 126.5873 |  |  |  | LOAD LIST |  |  | 2002.09/28 Ver 2.0
Transformer No. |  |  |  |  | [KVA] | type of Transformer |  | Demand [KVA] |  |  | 170.4856 | Demand [KVA] |  |  | 170.4856 | Reactor |  |  | Co.,Ltd.Yoshimura Airchitecture Design Office
[6 empty] | oil cooled |  | Ave.Power factor |  |  | 0.66983 | Ave.Power factor |  |  | 0.66983 |  |  |  | Electro Systems Engineering Service
Trunk | Board name |  | Load No. | Load name |  |  | Kind of | Rated Out | Number | Automatic Output(％) |  |  | Manual input(％) |  |  | Load | Input | Power F. | Demand | Demand | Demand | Demand | Note
No. | [6 empty] | load | -put[KW] |  | Eff. | Power F. | Load F. | Eff. | Power F. | Load F. | [KW] | [KVA] | of Load | factor | [KW] | [KVar] | [KVA]
0
72P1 | #7P-11 |  | Ana-019 | GC(PONA)(PEC) |  |  | others |  | 1 | [7 empty] | 11 | 80 | 0.4 | 3.52 | 2.64 | 4.4 |  | 0 | 8.8 | 6.6 | 11
| 1F-GC |  | Ana-020 | GC(GCD) |  |  | others |  | 1 | [7 empty] | 11 | 80 | 0.4 | 3.52 | 2.64 | 4.4 |  | 0 | 8.8 | 6.6 | 11
|  |  | Existing | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | Ana-024 | GC Fuel dilution |  |  | others |  | 1 | [7 empty] | 11 | 80 | 0.4 | 3.52 | 2.64 | 4.4 |  | 0 | 8.8 | 6.6 | 11
|  |  | Ana-137 | LC-MS |  |  | others |  | 1 | [7 empty] | 11 | 80 | 0.4 | 3.52 | 2.64 | 4.4 |  | 0 | 8.8 | 6.6 | 11
|  |  | Ana-136 | GC-MS (double convergence type) |  |  | others |  | 1 | [7 empty] | 7.5 | 80 | 0.4 | 2.4 | 1.8 | 3 |  | 0 | 6 | 4.5 | 7.5
|  |  | Ana-138 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
72P2 | #7P-11 |  | AC-127 | Air-conditioning exterior unit |  |  | IM-4P | 5.21 | 1 |  |  |  | 85 | 73 | 90 | 5.5165 |  |  | 0.8 | 4.4132 | 4.1317 | 6.0454 |  | 4.1317 | 5.5165 | 5.1647 | 7.5568
| 1F-GC |  | EH-127 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 3.5 | 95 | 0.8 | 2.66 | 0.8743 | 2.8 |  | 0 | 3.325 | 1.0929 | 3.5
|  |  | AC113 | Air-conditioning exterior unit |  |  | IM-4P | 4.37 | 1 |  |  |  | 85 | 73 | 90 | 4.6271 |  |  | 0.8 | 3.7016 | 3.4656 | 5.0707 |  | 3.4656 | 4.6271 | 4.332 | 6.3384
|  |  | EH-113 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 3.5 | 95 | 0.8 | 2.66 | 0.8743 | 2.8 |  | 0 | 3.325 | 1.0929 | 3.5
|  |  | AC-155 | Air-conditioning exterior unit |  |  | IM-4P | 9.12 | 1 |  |  |  | 85 | 80 | 90 | 9.6565 |  |  | 0.8 | 7.7252 | 5.7939 | 9.6565 |  | 5.7939 | 9.6565 | 7.2424 | 12.0706
|  |  | EH-155 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 8.7 | 95 | 0.8 | 6.612 | 2.1733 | 6.96 |  | 0 | 8.265 | 2.7166 | 8.7
|  |  | ACP-2-0 | Air-conditioning exterior unit |  |  | IM-4P | 15.64 | 1 |  |  |  | 85 | 80 | 90 | 16.56 |  |  | 0.8 | 13.248 | 9.936 | 16.56 |  | 9.936 | 16.56 | 12.42 | 20.7
0
0
0
0
0
72P3 | #7P-12 |  | Ana-058 | Hot wind drier |  |  | others |  | 1 | [7 empty] | 7 | 80 | 0.4 | 2.24 | 1.68 | 2.8 |  | 0 | 5.6 | 4.2 | 7
| 1F-ICP |  | Ana-059 | Ultrapure water manufacture M/C |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | Ana-042 | ICP luminescence analysis M/C |  |  | others |  | 1 | [7 empty] | 9 | 80 | 0.4 | 2.88 | 2.16 | 3.6 |  | 0 | 7.2 | 5.4 | 9
|  |  | Ana-040 | Atomic absorption spectrophotometer |  |  | others |  | 1 | [7 empty] | 11 | 80 | 0.4 | 3.52 | 2.64 | 4.4 | (Z-5000) | 0 | 8.8 | 6.6 | 11
|  |  | ACP-4-1 | Air-conditioning exterior unit |  |  | IM-4P | 4.86 | 1 |  |  |  | 85 | 73 | 90 | 5.1459 |  |  | 0.8 | 4.1167 | 3.8542 | 5.6393 |  | 3.8542 | 5.1459 | 4.8177 | 7.0492
|  |  | SF-8 | Supply fan |  |  | IM-4P | 0.2 | 1 |  |  |  | 70 | 65 | 90 | 0.25714 |  |  | 0.8 | 0.20571 | 0.24051 | 0.31648 |  | 0.24051 | 0.25714 | 0.30063 | 0.3956
|  |  | ACP-8-0 | Air-conditioning exterior unit |  |  | IM-4P | 7.99 | 1 |  |  |  | 85 | 80 | 90 | 8.46 |  |  | 0.8 | 6.768 | 5.076 | 8.46 |  | 5.076 | 8.46 | 6.345 | 10.575
|  |  | ACP-6-0 | Air-conditioning exterior unit |  |  | IM-4P | 1.36 | 1 |  |  |  | 80 | 70 | 90 | 1.53 |  |  | 0.8 | 1.224 | 1.2487 | 1.7486 |  | 1.2487 | 1.53 | 1.5609 | 2.1857
|  |  | ACP-7-0 | Air-conditioning exterior unit |  |  | IM-4P | 3.22 | 1 |  |  |  | 85 | 73 | 90 | 3.4094 |  |  | 0.8 | 2.7275 | 2.5536 | 3.7363 |  | 2.5536 | 3.4094 | 3.192 | 4.6704
|  |  | Ana-115 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | Ana-117 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | C-104 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
0
72P4 | #7P-13 |  | AC-137 | Air-conditioning exterior unit |  |  | IM-4P | 1.52 | 1 |  |  |  | 80 | 70 | 90 | 1.71 |  |  | 0.8 | 1.368 | 1.3956 | 1.9543 |  | 1.3956 | 1.71 | 1.7445 | 2.4429
| 1F-XPS | [22 empty] | 0
0
0
0
0
0
72P5 | #7P-21 |  | Existing | Draft chamber |  |  | IM-4P | 1.5 | 2 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 2.4832 |  |  | 0.4 | 0.99327 | 1.2055 | 1.562 |  | 1.2055 | 2.4832 | 3.0137 | 3.9049
| 2F-Atom |  | Ana-238 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | Ana-082 | Hot wind drier (for instrument) |  |  | others |  | 1 | [7 empty] | 11 |  | 0.4 | 0 | 4.4 | 4.4 |  | 0 | 0 | 11 | 11
|  |  | Ana-084-2 | Hot wind drier (for instrument) |  |  | others |  | 1 | [7 empty] | 26 |  | 0.4 | 0 | 10.4 | 10.4 |  | 0 | 0 | 26 | 26
|  |  | Ana-077 | Draft chamber |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
|  |  | AC-143 | Air-conditioning exterior unit |  |  | IM-4P | 9.29 | 1 |  |  |  | 85 | 80 | 90 | 9.8365 |  |  | 0.8 | 7.8692 | 5.9019 | 9.8365 |  | 5.9019 | 9.8365 | 7.3774 | 12.2956
|  |  | ACP-3-0 | Air-conditioning exterior unit |  |  | IM-4P | 5.98 | 1 |  |  |  | 85 | 73 | 90 | 6.3318 |  |  | 0.8 | 5.0654 | 4.7424 | 6.9389 |  | 4.7424 | 6.3318 | 5.928 | 8.6737
|  |  | ----- | Operation power supply |  |  | others |  | 1 | [7 empty] | 0.5 | 80 | 1 | 0.4 | 0.3 | 0.5 |  | 0 | 0.4 | 0.3 | 0.5
0
0
0
0
0
72P6 | #7P-22 |  |  | Draft chamber (for Ana-009) |  |  | IM-4P | 1.5 | 1 | 82.3727 | 63.5909 | 68.1818 |  |  |  | 1.2416 |  |  | 0.4 | 0.49663 | 0.60273 | 0.78098 |  | 0.60273 | 1.2416 | 1.5068 | 1.9525
| 2F-M/C-R/M |  | Ana-006 | XRF (RIX3000) |  |  | others |  | 1 | [7 empty] | 26 |  | 0.4 | 0 | 10.4 | 10.4 |  | 0 | 0 | 26 | 26
|  |  | Ana-009 | Data molding machine |  |  | others |  | 1 | [7 empty] | 7 |  | 0.4 | 0 | 2.8 | 2.8 |  | 0 | 0 | 7 | 7
|  |  | Ana-001 | Hot wind drier (for instrument) |  |  | others |  | 1 | [7 empty] | 17.5 |  | 0.4 | 0 | 7 | 7 |  | 0 | 0 | 17.5 | 17.5
|  |  | AC-127 | Air-conditioning exterior unit |  |  | IM-4P | 5.21 | 1 |  |  |  | 85 | 73 | 90 | 5.5165 |  |  | 0.8 | 4.4132 | 4.1317 | 6.0454 |  | 4.1317 | 5.5165 | 5.1647 | 7.5568
|  |  | EH-127 | ditto Booster heater |  |  | hearter |  | 1 | [7 empty] | 3.5 |  | 0.8 | 0 | 2.8 | 2.8 |  | 0 | 0 | 3.5 | 3.5
|  |  | ACP-9-0 | Air-conditioning exterior unit |  |  | IM-4P | 8.18 | 1 |  |  |  | 85 | 80 | 90 | 8.6612 |  |  | 0.8 | 6.9289 | 5.1967 | 8.6612 |  | 5.1967 | 8.6612 | 6.4959 | 10.8265
|  |  |  | Air-conditioning interior unit |  |  | IM-4P | 0.2 | 4 | 71.9545 | 65.0182 | 79.5455 |  |  |  | 0.8844 |  |  | 0.8 | 0.70752 | 0.82678 | 1.0882 |  | 0.82678 | 0.8844 | 1.0335 | 1.3602
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## DATA
Notes-1) Let the rate of load be the average value of the induction motor of the right above grade to Calculation axis power [KW] × (１＋ margin [%]).
Notes-2) The efficiency and powerfactor to the rate of load of an induction motor are computed by straight line proportionality calculation from a value 50 or 75,100%.
[10 empty] | Margin of motor selection[％]→ |  |  |  | 10
50Hz-200V |  |  |  | FEE,PF of Induction motor (50Hz-200V) | [5 empty] | 60Hz-220V |  |  |  | FEE,PF of Induction motor (60Hz-220V)
Output | Load | EFF(％) | PF(％) | at 50％ Load |  | at 75％ Load |  | at 100％ Load |  | Output | Load | EFF(％) | PF(％) | at 50％ Load |  | at 75％ Load |  | at 100％ Load
KW | factor |  |  | EFF(％) | PF(％) | EFF(％) | PF(％) | EFF(％) | PF(％) | KW | factor |  |  | EFF(％) | PF(％) | EFF(％) | PF(％) | EFF(％) | PF(％)
0.15 | [9 empty] | 0.15
0.2 | 79.5455 | 71.9545 | 65.0182 | 68.1 | 50.8 | 71.9 | 63.4 | 72.2 | 72.3 | 0.2 | 79.5455 | 75.0909 | 64.6273 | 71.1 | 51.2 | 75 | 63.1 | 75.5 | 71.5
0.4 | 68.1818 | 75.9818 | 65.8273 | 74.6 | 57.1 | 76.5 | 69.1 | 76 | 77.8 | 0.4 | 68.1818 | 78.6 | 66.5091 | 77 | 58 | 79.2 | 69.7 | 78.8 | 77.2
0.75 | 69.697 | 80.4909 | 65.4061 | 78.6 | 55.4 | 81 | 68.1 | 80.5 | 76 | 0.75 | 69.697 | 83.2121 | 66.2697 | 81.4 | 56.5 | 83.7 | 68.9 | 83.3 | 76.2
1.5 | 68.1818 | 82.3727 | 63.5909 | 80.7 | 54.5 | 83 | 67 | 83.1 | 75.1 | 1.5 | 68.1818 | 85.1818 | 57.2091 | 83.8 | 55.1 | 85.7 | 58 | 85.8 | 75.9
2.2 | 76.4463 | 86.6653 | 72.1992 | 85.4 | 59.6 | 86.7 | 71.8 | 86.1 | 78.7 | 2.2 | 76.4463 | 88.5942 | 73.1818 | 87.4 | 61 | 88.6 | 72.8 | 88.5 | 79.4
3.7 | 72.4816 | 87.0396 | 72.4912 | 86.5 | 61.7 | 87.1 | 73.7 | 86.3 | 80.4 | 3.7 | 72.4816 | 88.4093 | 73.0214 | 87.6 | 62.5 | 88.5 | 74.2 | 88.1 | 80.6
5.5 | 76.0331 | 89.2835 | 75.881 | 88.3 | 63.4 | 89.3 | 75.6 | 88.9 | 82.4 | 5.5 | 76.0331 | 90.1959 | 77.6314 | 89 | 66.1 | 90.2 | 77.4 | 90.1 | 83
7.5 | 78.7879 | 89.4242 | 78.3939 | 88.8 | 65.3 | 89.5 | 77.5 | 89 | 83.4 | 7.5 | 78.7879 | 90.4545 | 79.3727 | 89.6 | 67.5 | 90.5 | 78.6 | 90.2 | 83.7
11 | 76.4463 | 91.8769 | 76.4587 | 91.3 | 64.7 | 91.9 | 76.1 | 91.5 | 82.3 | 11 | 76.4463 | 92.5884 | 77.7298 | 92 | 67.4 | 92.6 | 77.4 | 92.4 | 83.1
15 | 78.7879 | 92.2697 | 78.3788 | 91.6 | 66.3 | 92.3 | 77.5 | 92.1 | 83.3 | 15 | 78.7879 | 92.6848 | 80.1121 | 91.8 | 68.4 | 92.7 | 79.4 | 92.6 | 84.1
18.5 | 82.3096 | 92.8 | 78.1251 | 91.9 | 64.5 | 92.8 | 76.4 | 92.8 | 82.3 | 18.5 | 82.3096 | 93.2292 | 80.0789 | 92.3 | 67.7 | 93.2 | 78.5 | 93.3 | 83.9
22 | 83.6777 | 93.0612 | 81.5967 | 92.7 | 69.1 | 93.2 | 80 | 92.8 | 84.6 | 22 | 83.6777 | 93.5306 | 82.6537 | 92.9 | 71.8 | 93.6 | 81.3 | 93.4 | 85.2
30 | 78.7879 | 92.9242 | 80.0121 | 92.7 | 68.1 | 93 | 79.3 | 92.5 | 84 | 30 | 78.7879 | 93.2848 | 82.2364 | 92.6 | 72.1 | 93.3 | 81.6 | 93.2 | 85.8
37 | 82.3096 | 93.9953 | 85.5894 | 93.9 | 77.1 | 94.2 | 84.8 | 93.5 | 87.5 | 37 | 82.3096 | 93.6538 | 86.5187 | 93.1 | 79.1 | 93.8 | 85.7 | 93.3 | 88.5
45 | 82.8283 | 92.8374 | 82.2838 | 92.4 | 70.7 | 92.9 | 81 | 92.7 | 85.1 | 45 | 82.8283 | 93.7061 | 84.8646 | 93.2 | 75.5 | 93.8 | 83.8 | 93.5 | 87.2
55 | 82.6446 | 94.0083 | 80.8653 | 93.9 | 68.4 | 94.1 | 79 | 93.8 | 85.1 | 55 | 82.6446 | 94.5388 | 83.576 | 94.1 | 73 | 94.6 | 82.2 | 94.4 | 86.7
ＤＡＴＡ ｓｈｅｅｔ
Note on G7: 三菱電機株式会社 高性能省エネモータ スーパーラインエコシリーズ （２００１年１０月）
Note on S7: 三菱電機株式会社 高性能省エネモータ スーパーラインエコシリーズ （２００１年１０月）